## Sheet1
BOQ Item Sr No(unique no - alphanumeric) | HSN / SAC Code (Numeric) | Item Description(Text) | Unit(Text) | Scheduled Qty(Numeric) | Design Qty(Numeric) | Rate Basic(Numeric) | GST %(Numeric) | Non-Scheduled(Yes/No)
1 | 995461 | SITC of Electric Motor driven Fire Pump set of 2400 LPM @70 m head with a) pump with bronze impellar, b)motor, c) coupling, d) base plate, e) foundation bolts matching flanges with gasket and fastners with all complete. | Nos | 1 | 0 | 392000 | 18 | N
2 | 995461 | SITC of Electric Motor drive Jockey fire pump set of 280LPM @70 mtrs head with a) pump with bronze impellar, b) motor, c) base plate, d) foundation bolts, e) mating flanges with gasket and fastners with all complete. | Nos | 1 | 0 | 158200 | 18 | N
3 | 995461 | Electric driven Booster Pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal and floor of 900 lpm @ 35M conforming to IS: 5120. Suitable HP, SQ cage induction motor suitable for operation on 415 volts, | Nos | 1 | 0 | 112000 | 18 | N
4 | 995461 | SITC of Electric Motor Starter Control Panel, Compartmentalised Floor mounted type, as per TAC requirement, for the Auto / Manual Operations of the above 2 Pump sets along with the Power & Control Cabling, from the Pump set Drives to Control Panel (each 8.0 M. length Max) with Earthing & Inter-locking, having, MCCB Switches, Meters, Fuses,Audio / Visual Alarms and Indicating Lamps, with Direct-On-Line Starters for Jokey Pump set & star delta operation for main pump Drives of Hydrant System,with Sequential Operation Circuitries. | Nos | 1 | 0 | 448000 | 18 | N
5 | 995461 | SITC of Pressure Gauges with Syphon Tube and Cock 150mm Dial Range - 0 to 1kg /cm2. | Nos | 3 | 0 | 3290 | 18 | N
6 | 995461 | SITC of Pressure Switches with Tubing, Control Cabling upto Panel, complete | Nos | 2 | 0 | 2590 | 18 | N
7a | 995461 | 200 mm NB Class " C " | Mtr | 6 | 0 | 4956 | 18 | N
7 b | 995461 | 150 mm NB Class " C " | Mtr | 6 | 0 | 4032 | 18 | N
7 c | 995461 | 100mm NB 'C' Class | Mtr | 6 | 0 | 2660 | 18 | N
7 d | 995461 | 80mm NB 'C' Class | Mtr | 6 | 0 | 1890 | 18 | N
7 e | 995461 | 65mm NB 'C' Class | Mtr | 6 | 0 | 1521.8 | 18 | N
7 f | 995461 | 50mm NB 'C' Class | Mtr | 6 | 0 | 1204 | 18 | N
7 g | 995461 | 25mm NB 'C' Class | Mtr | 6 | 0 | 602 | 18 | N
8a | 995461 | 150mm NB double flanged wafer type lever operated / wheel operated butterfly valve | Nos | 3 | 0 | 8610 | 18 | N
8 b | 995461 | 80mm NB double flanged wafer type lever operated / wheel operated butterfly valve | Nos | 1 | 0 | 4130 | 18 | N
8 c | 995461 | 65mm NB double flanged wafer type lever operated / wheel operated butterfly valve | Nos | 1 | 0 | 3745 | 18 | N
9a | 995461 | 150mm NB Non Return Valves | Nos | 2 | 0 | 13160 | 18 | N
9 b | 995461 | 65mmNB Non Return Valves | Nos | 1 | 0 | 6125 | 18 | N
10 | 995461 | SITC of Air Vessel Tank 300 NB x 1.2 mtrs. | Nos | 1 | 0 | 28140 | 18 | N
11a | 995461 | 50 NB Ball Valve | Nos | 3 | 0 | 3157 | 18 | N
11 b | 995461 | 25 NB Ball Valve | Nos | 4 | 0 | 1149.75 | 18 | N
12 | 995461 | SITC of 150 NB Fourway Fire Brigade Inlet Connection having inbuilt non.return valve with 04 nos of 63 mm SS instantaneaous inlets for fire water tank. | Nos | 1 | 0 | 9800 | 18 | N
13 | 995461 | SITC of 25 NB Air Realease Valve | Nos | 1 | 0 | 1750 | 18 | N
14 | 995461 | Structural Steel Support | KG | 500 | 0 | 140 | 18 | N
15 | 995461 | Cabling from motor to Starter with copper earthing Strip within the pumphouse | Mtr | 60 | 0 | 2143.75 | 18 | N
16 | 995461 | S/I/T/C of Water Storage Tank of Capacity 25,000.00 Ltrs./or 80,000.00 Ltrs.total aggregate capacity will be 150,000.00 Ltrs | Lumpsum | 1 | 0 | 2170000 | 18 | N
2.1 a | 995461 | 150mm NB 'C' GI ERW Pipe as Per IS : 3589 / 6.3mm thick & IS 1239 / II 'C' Class | Mtr | 24 | 0 | 4319 | 18 | N
2.1 b | 995461 | 100mm NB 'C' GI ERW Pipe as Per IS : 3589 / 6.3mm thick & IS 1239 / II 'C' Class | Mtr | 12 | 0 | 2849 | 18 | N
2.1 c | 995461 | 80mm NB 'C' GI ERW Pipe as Per IS : 3589 / 6.3mm thick & IS 1239 / II 'C' Class | Mtr | 12 | 0 | 2023 | 18 | N
2.2 a | 995461 | 150mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 | Mtr | 390 | 0 | 4032 | 18 | N
2.2 b | 995461 | 100mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 | Mtr | 180 | 0 | 2660 | 18 | N
2.2 c | 995461 | 80mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 | Mtr | 48 | 0 | 1890 | 18 | N
2.3 a | 995461 | 150 NB double flanged wafer type lever operated / wheel operated butterfly valve of 200 | Nos | 8 | 0 | 8960 | 18 | N
2.3 b | 995461 | 100 NB double flanged wafer type lever operated / wheel operated butterfly valve of 200 | Nos | 10 | 0 | 1540 | 18 | N
2.4 a | 995461 | External oblique type stainless steel single headed hydrant valve | Nos | 12 | 0 | 8680 | 18 | N
2.4 b | 995461 | Internal oblique type stainless steel single headed hydrant valve | Nos | 10 | 0 | 8680 | 18 | N
2.5 a | 995461 | External M. S. Hose Box of size 750 x 600 x 250mm | Nos | 12 | 0 | 5600 | 18 | N
2.5 b | 995461 | Internal M. S. Hose Box of size 750 x 600 x 250mm | Nos | 10 | 0 | 5600 | 18 | N
2.6 | 995461 | SITC of 63mm dia stainless steel universal branch pipe as per IS 2871 | Nos | 22 | 0 | 2660 | 18 | N
2.7 | 995461 | Fire fighting hose as per IS 14933 ( Type -A) . The fire hose shall be 15 mtrs long | Nos | 44 | 0 | 4550 | 18 | N
2.8 | 995461 | 25mm NB SITC of GM air release valve . | Nos | 5 | 0 | 1820 | 18 | N
2.9 | 995461 | SITC of swinging type M .S. Hose Reel drum of red powerd coated finish with 30 mtrs x 25mm Dia rubber hose as per IS 884. | Nos | 10 | 0 | 9520 | 18 | N
2.1 | 995461 | SITC of Ball Valve 25NB | Nos | 27 | 0 | 1050 | 18 | N
2.11 | 995461 | SITC of 150NB Four way Siamese Connection for hydant network with 4 nos. of 63 mm instantaneaous inlets in glass fronted wall box having inbuilt non return valve and 150mm BFV with fittings,nut,bolts & washers. | Nos | 1 | 0 | 13300 | 18 | N
2.12 | 995461 | SITC of RCC hume pipe NP3 class (300 mm dia) with collar & joining material for road crossing | Mtrs. | 30 | 0 | 3360 | 18 | N
2.13 | 995461 | Structural Steel Support | KG | 2000 | 0 | 140 | 18 | N
3.1 | 995461 | SITC of Standard response Pendent type Brass sprinklers with Nickel chrome plated finish- K 80, T- 68 deg.c, 15mm end connection | Nos | 438 | 0 | 518 | 18 | N
3.2 | 995461 | SITC of Standard response Upright type Brass sprinklers with Nickel chrome plated finish- K 80, T- 68 deg.c, 15mm end connection | Nos | 614 | 0 | 588 | 18 | N
3.3 | 995461 | SS Flexible Drop 1500mm/1200mm Length | Nos | 438 | 0 | 2730 | 18 | N
3.4 a | 995461 | 150 mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 / I- 'C' Class | Mtrs | 180 | 0 | 4032 | 18 | N
3.4 b | 995461 | 100 mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 / I- 'C' Class | Mtrs | 230 | 0 | 2660 | 18 | N
3.4 c | 995461 | 80 mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 / I- 'C' Class | Mtrs | 410 | 0 | 1890 | 18 | N
3.4 d | 995461 | 50 mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 / I- 'C' Class | Mtrs | 210 | 0 | 1204 | 18 | N
3.4 e | 995461 | 40 mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 / I- 'C' Class | Mtrs | 536 | 0 | 911.4 | 18 | N
3.4 f | 995461 | 32 mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 / I- 'C' Class | Mtrs | 66 | 0 | 773.5 | 18 | N
3.4 g | 995461 | 25 mm NB 'C' Class GI ERW Pipe as Per IS : 3589 / 6.3mm thick Gr. Fe 410 & IS 1239 / I- 'C' Class | Mtrs | 820 | 0 | 602 | 18 | N
3.5 | 995461 | SITC of Cast Iron Wet Alarm Control valve, internally and externally painted, pre-trimmed with bi-pass connection, test and drain connection, tested to 1.5 times the working pressure, with pressure gauge, water motor gong, including matching flanges, bolts/studs, nuts, washers & gaskets of 150 mm. | Nos | 2 | 0 | 57400 | 18 | N
3.6 | 995461 | SITC of double flanged wafer type lever operated / wheel operated butterfly valve of 200 psi rating including matching flanges, bolts/studs, nuts, washers & gaskets. 150 mm | Nos | 2 | 0 | 9380 | 18 | N
3.7 | 995461 | SITC of Water flow switch of 150 mm | Nos | 2 | 0 | 7000 | 18 | N
4.1 a | 995461 | 5 kg.Capacity Clean Agent Fire Extinguishers with stand | Nos | 57 | 0 | 40600 | 18 | N
4.1 b | 995461 | CO2 fire extinguishers 4.5 kg | Nos | 4 | 0 | 6580 | 18 | N
4.1 c | 995461 | Fire Buckets Set ( 04 Buckets in one set ) | Nos | 1 | 0 | 4900 | 18 | N
4.1 d | 995461 | Safety Signages for staircase and evacuation | Nos | 50 | 0 | 1400 | 18 | N
5.1 | 995461 | Dismantling and Re-Erection of Existing Pump i.e. Diesel Pump, with Diesel Tank Fuel Piping, Main Pump and Jockey Pump along with accessories and Cabling, and Electrical control Panel | Job | 1 | 0 | 350000 | 18 | N
6.1 | 995461 | Construction of Pump House for housing for Main Pump 2 Nos. Diesel Pump 1 No. Jockey Pump 2 Nos. Air Vessel tank 1 No. Space for seating of 6 nos. Staff, made out of galvalume sheet as per following details : | Job | 1 | 0 | 2170000 | 18 | N
7.1 a | 995461 | a. Excavation in Soft Soil | Cu.Mtrs. | 100 | 0 | 1400 | 18 | N
7.1 b | 995461 | b) Excavation in Soft soil | Cu.Mtrs. | 20 | 0 | 1750 | 18 | N
7.1 c | 995461 | c ) Excavtion in Hard rock | Cu.Mtrs. | 10 | 0 | 2100 | 18 | N
8.1 | 995461 | PCC 1: 4 : 8 for Above Ground Pipe Support with " U " Clamp | Cu.Mtrs. | 25 | 0 | 9828 | 18 | N
9.1 | 995461 | Providing and laying Design-Mix Reinforced Cement Concrete foundation for various pumps of M-20 by weight batching using graded stone aggregate of 20 mm maximum size including mechanical mixing and vibration, consolidation, finishing, curing etc. as specified and also including dewatering, if any, cost of form work, shuttering & steel reinforcement, including nozing all around by 50 x 50 x 5 mm angle. | Cu.Mtrs. | 4 | 0 | 16100 | 18 | N
10.1 | 995461 | Labour and Transport | Job | 1 | 0 | 140000 | 18 | N
11.1 | 995461 | Packing and Forwarding | Job | 1 | 0 | 70000 | 18 | N
12.1 | 995461 | Transit Insurance | Lumpsum | 1 | 0 | 14000 | 18 | N
13.1 | 995461 | Comprehensive Insurance | Lumpsum | 1 | 0 | 21000 | 18 | N
14.1 | 995461 | Design, Installation, Testing, Commissioning of Pressurised Water Yard Hydrant System (PWYHS) inclusive of Automatic Sprinkler System at Administration Building at JNPT.” | Job | 1 | 0 | 700000 | 18 | N
15.1 | 995461 | Transportation & Labour charges | Job | 1 | 0 | 70000 | 18 | N
16.1 | 995461 | Manning for operation and complete technical management of PWYHS, APADS and Sprinkler system at JNPT Administration Building for period of 3 years ( 7 No Fireman , 1 Electrician cum pump operator and 1 System Administration cum supervisor ) | Job | 1 | 0 | 8658000 | 18 | N