## Sheet1
BOQ Item Sr No(unique no - alphanumeric) | HSN / SAC Code (Numeric) | Item Description(Text) | Unit(Text) | Scheduled Qty(Numeric) | Design Qty(Numeric) | Rate Basic(Numeric) | GST %(Numeric) | Non-Scheduled(Yes/No)
1 |  | New Pumps Inside Fire Water Pump House
2 | 84137094 | New Vertical turbine Main Fire water pump along with Diesel Engine-1440 M3/hr @ 145 MWC Head (As per OISD-156 requirment) SUCTION HEAD APPROX 9 METERS | Nos. | 2 | 2 | 56640000 | 18 | N
3 | 84137094 | New Vertical turbine Jockey pump with electric motor -216 M3/hr @ 150 MWC Head-New (As per OISD-156 requirment) SUCTION HEAD APPROX 9 METERS | Nos. | 2 | 2 | 14714600 | 18 | N
4 |  | Existing Pumps and equipment Inside Fire Water Pump House DISTAMNTLING FROM EXISTING PUMP HOUSE AND , SHIFTING, INSTALLATION TESTING AND COMMISIONING AT NEW PUMP HOUSE AT APPROX DISTANCE OF 300 METERS
5 | 84137094 | Existing Vertical turbine Main Fire water pump (Diesel egine)-1440 M3/hr @ 145 MWC Head (As per OISD-156 requirment) | Nos. | 2 | 2 | 741040 | 18 | N
6 | 84137094 | Existing Vertical turbine Main Fire water pump (Motor Drive)-1440 M3/hr, (Motor rating 890KW) @ 145 MWC Head-Existing (As per OISD-156 requirment) | No. | 1 | 1 | 741040 | 18 | N
7 | 84798999 | Existing Hydro-pneumatic Tank-3000L | No. | 1 | 1 | 92630 | 18 | N
8 | 84144030 | Existing Air Compressor-5HP | No. | 1 | 1 | 92630 | 18 | N
9 |  | New Piping & Valves
10 | 73041120 | 600NB Pipe (CS as per IS:3589/IS:1239) 10mm thick, with cement line/ poly glass lined | Mtr | 137.5 | 137.5 | 41878 | 18 | N
11 | 73041120 | 300NB Pipe (CS as per IS:3589/IS:1239) 8mm thick with cement line/ poly glass lined | Mtr | 6 | 6 | 15954 | 18 | N
12 | 73041120 | 150NB Pipe (CS as per IS:3589/IS:1239) with cement line/ poly glass lined | Mtr | 18 | 18 | 6443 | 18 | N
13 | 73041120 | 50NB Pipe (CS as per IS:3589/IS:1239) with cement line/ poly glass lined | Mtr | 18 | 18 | 2454 | 18 | N
14 | 84818090 | Motorized Gate Valve-600NB, Isolation valves shall be flanged gate valves with stem, outside screw, yoke and indicator, manufactured to BS 5150 / DIN 3230 part 4 / DIN 3352, face-to-face dimension to BS 5163 type A (ISO 5752 S.3), flanges and drilling to ISO 7005-2 (BS EN 1092-2: 1997, DIN 2501). Gate valves shall be fitted with a seating trim manufactured from zinc-free bronze. Seals and wedge covering shall be manufactured from EPDM rubber. Valves shall incorporate seat plugs for the removal of debris. The valve assembly shall be conforming to BS EN 1074-2 and OISD-156 & technical specification requirement. | Nos. | 5 | 5 | 685462 | 18 | N
15 | 84818090 | Motorized GateValve-150NB, Isolation valves shall be flanged gate valves with stem, outside screw, yoke and indicator, manufactured to BS 5150 / DIN 3230 part 4 / DIN 3352, face-to-face dimension to BS 5163 type A (ISO 5752 S.3), flanges and drilling to ISO 7005-2 (BS EN 1092-2: 1997, DIN 2501). Gate valves shall be fitted with a seating trim manufactured from zinc-free bronze. Seals and wedge covering shall be manufactured from EPDM rubber. Valves shall incorporate seat plugs for the removal of debris. The valve assembly shall be conforming to BS EN 1074-2 and OISD-156 & technical specification requirement. | Nos. | 2 | 2 | 153766 | 18 | N
16 | 84818090 | Gate Valve-600NB, Isolation valves shall be flanged gate valves with stem, outside screw, yoke and indicator, manufactured to BS 5150 / DIN 3230 part 4 / DIN 3352, face-to-face dimension to BS 5163 type A (ISO 5752 S.3), flanges and drilling to ISO 7005-2 (BS EN 1092-2: 1997, DIN 2501). Gate valves shall be fitted with a seating trim manufactured from zinc-free bronze. Seals and wedge covering shall be manufactured from EPDM rubber. Valves shall incorporate seat plugs for the removal of debris. The valve assembly shall be conforming to BS EN 1074-2 and OISD-156 & technical specification requirement. | No. | 1 | 1 | 500202 | 18 | N
17 | 84818090 | Gate Valve-300NB, Isolation valves shall be flanged gate valves with stem, outside screw, yoke and indicator, manufactured to BS 5150 / DIN 3230 part 4 / DIN 3352, face-to-face dimension to BS 5163 type A (ISO 5752 S.3), flanges and drilling to ISO 7005-2 (BS EN 1092-2: 1997, DIN 2501). Gate valves shall be fitted with a seating trim manufactured from zinc-free bronze. Seals and wedge covering shall be manufactured from EPDM rubber. Valves shall incorporate seat plugs for the removal of debris. The valve assembly shall be conforming to BS EN 1074-2 and OISD-156 & technical specification requirement. | No. | 1 | 1 | 190818 | 18 | N
18 | 84818090 | Gate Valve-100NB, Isolation valves shall be flanged gate valves with stem, outside screw, yoke and indicator, manufactured to BS 5150 / DIN 3230 part 4 / DIN 3352, face-to-face dimension to BS 5163 type A (ISO 5752 S.3), flanges and drilling to ISO 7005-2 (BS EN 1092-2: 1997, DIN 2501). Gate valves shall be fitted with a seating trim manufactured from zinc-free bronze. Seals and wedge covering shall be manufactured from EPDM rubber. Valves shall incorporate seat plugs for the removal of debris. The valve assembly shall be conforming to BS EN 1074-2 and OISD-156 & technical specification requirement. | Nos. | 5 | 5 | 54652 | 18 | N
19 | 84818090 | Gate Valve-50NB, Isolation valves shall be flanged gate valves with stem, outside screw, yoke and indicator, manufactured to BS 5150 / DIN 3230 part 4 / DIN 3352, face-to-face dimension to BS 5163 type A (ISO 5752 S.3), flanges and drilling to ISO 7005-2 (BS EN 1092-2: 1997, DIN 2501). Gate valves shall be fitted with a seating trim manufactured from zinc-free bronze. Seals and wedge covering shall be manufactured from EPDM rubber. Valves shall incorporate seat plugs for the removal of debris. The valve assembly shall be conforming to BS EN 1074-2 and OISD-156 & technical specification requirement. | Nos. | 4 | 4 | 24084 | 18 | N
20 | 84818090 | Gate Valve-15NB, Isolation valves shall be flanged gate valves with stem, outside screw, yoke and indicator, manufactured to BS 5150 / DIN 3230 part 4 / DIN 3352, face-to-face dimension to BS 5163 type A (ISO 5752 S.3), flanges and drilling to ISO 7005-2 (BS EN 1092-2: 1997, DIN 2501). Gate valves shall be fitted with a seating trim manufactured from zinc-free bronze. Seals and wedge covering shall be manufactured from EPDM rubber. Valves shall incorporate seat plugs for the removal of debris. The valve assembly shall be conforming to BS EN 1074-2 and OISD-156 & technical specification requirement. | Nos. | 2 | 2 | 5652 | 18 | N
21 | 84818090 | Non-Return Valve-600NB, IS : 5312 Swing check type reflux (non-return) valves Part I (Part I) single door pattern and as per OISD-156 & technical specification requirement. | Nos. | 5 | 5 | 466855 | 18 | N
22 | 84818090 | Non-Return Valve-150NB, IS : 5312 Swing check type reflux (non-return) valves Part I (Part I) single door pattern and as per OISD-156 & technical specification requirement. | Nos. | 6 | 6 | 154692 | 18 | N
23 | 84818090 | Non-Return Valve-25NB, IS : 5312 Swing check type reflux (non-return) valves Part I (Part I) single door pattern and as per OISD-156 & technical specification requirement. | No. | 1 | 1 | 4632 | 18 | N
24 | 84818090 | Niddle Valve-25NB as per OISD-156 & technical specification requirement. | No. | 1 | 1 | 4076 | 18 | N
25 | 84818090 | Niddle Valve-15NB as per OISD-156 & technical specification requirement. | Nos. | 17 | 17 | 2594 | 18 | N
26 | 84818090 | Pressure Relief Valve | Nos. | 2 | 2 | 6669 | 18 | N
27 | 84261100 | EOT Crane- 7.5 Ton Capacity | No. | 1 | 1 | 1148612 | 18 | N
28 | 7309 | 15 KL steel tank for HSD storage with level transmitter, Flowmeter and switch at FCB with 2nos. pumps of 3KL per Hour capacity and 65NB piping length of 300 meters (approx.) to TCB pump house with 11 nos. isolation ball valves etc., including associated electrical works. | LS | 1 | 1 | 963352 | 18 | N
29 |  | HT Panel
30 | 85352129 | 3.3 KV HT VCB Panel with 1 I/C, 4 Outgoing feeder (630A) including spare Feeder 630 A VCB with necessary CT, VT, metering & protections | No. | 1 | 1 | 4248000 | 18 | N
31 | 853720 | LV Switchgear: 415V, 3phase, 4 wire, 50 Hz, 1600A, 50 KA for 1second, double front fully draw out type PMCC comprising of ACBs, CTs/PTs, relays, indicating lamps etc. as per attached SLDs, specifications & DS including weather proof double compression Ni plated brass cable glands and lugs for all incoming and outgoing feeders and including supply of commissioning and 2 years O&M spares. | No. | 1 | 1 | 1298000 | 18 | N
32 | 85321000 | CAPACITOR PANEL : 3.3 KV, 3Ph-N, 50Hz, 25KA for 1second, 500KVAR capacitor panel with capacitors and APFC relay, protections, filters etc. including weather proof double compression Ni plated brass cable glands and lugs for all incoming and outgoing feeders and including supply of commissioning and 2 years O&M spares. | No. | 1 | 1 | 1652000 | 18 | N
33 | 85321000 | CAPACITOR PANEL : 415 V, 3Ph-N, 50Hz, 50 KA for 1second, 100KVAR capacitor panel with capacitors and APFC relay, protections, filters etc. including weather proof double compression Ni plated brass cable glands and lugs for all incoming and outgoing feeders and including supply of commissioning and 2 years O&M spares. | No. | 1 | 1 | 413000 | 18 | N
34 |  | LDB and SUB-LDB
35 | 85371000 | LDB / LP, Weatherproof, IP 65, incomer 63A, 3 Phase, 4 wire, 12 Way LDB, 10kA for 1 sec with RCBO | No. | 1 | 1 | 60357 | 18 | N
36 | 85044090 | UPSDB for critical lighting | No. | 1 | 1 | 130774 | 18 | N
37 |  | Transformer
38 | 850434 | 750 KVA, 3.3 KV/0.433 KV, Dyn11, AN type with on load tap changer power transformer complete with weather proof double compression Ni plated brass cable glands and cable lugs for all incoming and outgoing cables and all other accessories and as per attached specifications & DS including supply of commissioning and 2 years O&M spares. | No. | 1 | 1 | 4838000 | 18 | N
39 |  | BATTERY CHARGER WITH BATTERY & DC DB
40 | 85044030 | 110V, BATTERY CHARGER consisting of dual float cum boost charger and Ni-Cd type battery with two hour back up capacity for above HT and LT breaker including supply of commissioning and 2 years O&M spares. | No. | 1 | 1 | 271607 | 18 | N
41 | 85381090 | DC DISTRIBUTION BOARD: 110V DC, 2 wire 63A DC Distribution Board fed by duel float cum boost charger including supply of commissioning and 2 years O&M spares. Incomer: 63A DP MCB Outgoing: 15nos. 16A DP MCB | No. | 1 | 1 | 37217 | 18 | N
42 |  | LIGHTING FIXTURES & ACCESSORIES
43 | 94052100 | 230 Volt AC, 80W well glass units,LED lighting fixtures and all other accessories for fire water pump house | Nos. | 25 | 25 | 4975 | 18 | N
44 | 94052100 | 230 Volt AC, 80W well glass units,LED lighting fixtures and all other accessories for fire water pump house with 1hr battery backup. | Nos. | 5 | 5 | 11669 | 18 | N
45 | 94052100 | 230 Volt AC, 40W LED lighting fixtures indoor use and all other accessories for electrical room | Nos. | 30 | 30 | 4024 | 18 | N
46 | 94052100 | 230 Volt AC, 40W LED lighting fixtures indoor use and all other accessories for electrical room with 1hr battery backup. | Nos. | 5 | 5 | 5782 | 18 | N
47 | 94051090 | 230 Volt AC, 40W LED lighting fixtures flameproof and all other accessories for battery room | Nos. | 2 | 2 | 10148 | 18 | N
48 | 94052100 | 230 Volt AC, 1x18 W LED lighting fixtures indoor use and all other accessories for electrical room | Nos. | 5 | 5 | 3219 | 18 | N
49 | 94051020 | Exit Light | Nos. | 5 | 5 | 6767 | 18 | N
50 | 85446090 | Lighting Wire | m | 600 | 600 | 79 | 18 | N
51 | 8537109120 | 6A indoor Switch board | Nos. | 10 | 10 | 2194 | 18 | N
52 | 85361040 | 6A FLP Switch | Nos. | 2 | 2 | 3381 | 18 | N
53 |  | JUNCTION BOX
54 | 85369030 | 240 Volt AC, 16 A, Cast Aluminium weatherproof 4-way, 125 mm (minimum) internal dimensions junction box with terminals block suitable for 2.5 sq.mm along with weatherproof double compression Ni plated brass cables glands for all incoming and outgoing cables,PVC shroud and other accessories. | Nos. | 100 | 100 | 5853 | 18 | N
55 |  | RECEPTACLES
56 |  | Weatherproof Interlocking type switch sockets and plugs of following ratings as per attached specifications. All switch sockets shall be provided with 3mm thick FRP canopy with side cover and required no. of double compression stainless steel cable glands and stopping plug.
57 | 85371000 | i) 415V, 5-pin, 63A Welding Receptacle weatherproof switch socket and plug | No. | 1 | 1 | 9328 | 18 | N
58 | 85371000 | ii) 240V, 3-pin, 16A/5A weatherproof switch socket and plug | Nos. | 15 | 15 | 6036 | 18 | N
59 |  | RIGID/ FLEXIBLE CONDUIT
60 | 39172930 | 25 mm Dia. Heavy duty Rigid PVC Conduit of minimum 2.0 mm thick of wall with all accessories like bends, elbow etc and as per IS 2509. " | m | 625 | 625 | 137 | 18 | N
61 | 73059010 | 100 mm dia GI conduit - Class-B Galvanized Iron (G.I. pipes) conforming to IS-1239 complete with accessories (bends, reducers, couplers etc.) of following sizes:- 100 mm NB | m | 150 | 150 | 3015 | 18 | N
62 |  | HT/ LT CABLES AS PER ENCLOSED SPECIFICATIONS
63 |  | 3.3KV(UE) armoured XLPE, FRLS Power Cable of following size:-
64 | 85444919 | 3C x 150 sqmm (AL) | m | 265 | 265 | 2195 | 18 | N
65 |  | 1.1KV(E) armoured XLPE, FRLS Power Cable of following size:-
66 | 85444919 | 3.5C x 240, Sqmm XLPE AL | m | 350 | 350 | 2138 | 18 | N
67 | 85444919 | 4C X 25, Sqmm XLPE AL | m | 300 | 300 | 453 | 18 | N
68 | 85444919 | 4C X 10, Sqmm XLPE AL | m | 210 | 210 | 307 | 18 | N
69 | 85444919 | 4C X 2.5, Sqmm XLPE AL | m | 540 | 540 | 205 | 18 | N
70 | 85444919 | 3C X 2.5, Sqmm XLPE AL | m | 50 | 50 | 177 | 18 | N
71 | 85444919 | 2C X 2.5, Sqmm XLPE AL | m | 50 | 50 | 156 | 18 | N
72 | 85444919 | 2C X 4, Sqmm XLPE AL | m | 265 | 265 | 112 | 18 | N
73 | 85444919 | 2C X 16, Sqmm XLPE AL | m | 300 | 300 | 342 | 18 | N
74 | 85444919 | 1.1KV(E) armoured XLPE, FRLS Control Cable of following size:-
75 | 85444919 | 7C x 2.5 SQMM CU | m | 1000 | 1000 | 531 | 18 | N
76 | 85444919 | 3C x 2.5 SQMM CU | m | 100 | 100 | 283 | 18 | N
77 |  | END TERMINATION KIT
78 | 85469010 | Heat shrinkable end termination kit suitable for 3.3KV (UE) XLPE, FRLS cables of following sizes.
79 | 85469010 | 3C x 150 sqmm (AL) ( suitable for indoor purpose) | Nos. | 8 | 8 | 20393 | 18 | N
80 |  | CABLE LUGS
81 |  | Crimping type heavy duty, long barrel Tinned Cu /Al lugs for all Al and Cu cables as the case may be for the following size for indoor use:-
82 | 85359090 | 3.5C x 240, Sqmm XLPE AL | Nos. | 50 | 50 | 732 | 18 | N
83 | 85359090 | 4C X 25, Sqmm XLPE AL | Nos. | 40 | 40 | 420 | 18 | N
84 | 85359090 | 4C X 10, Sqmm XLPE AL | Nos. | 20 | 20 | 366 | 18 | N
85 | 85359090 | 4C X 2.5, Sqmm XLPE AL | Nos. | 40 | 40 | 313 | 18 | N
86 | 85359090 | 3C X 2.5, Sqmm XLPE AL | Nos. | 24 | 24 | 313 | 18 | N
87 | 85359090 | 2C X 2.5, Sqmm XLPE AL | Nos. | 20 | 20 | 313 | 18 | N
88 | 85359090 | 2C X 4, Sqmm XLPE AL | Nos. | 20 | 20 | 348 | 18 | N
89 | 85359090 | 2C X 16, Sqmm XLPE AL | Nos. | 20 | 20 | 366 | 18 | N
90 | 85359090 | 7C x 2.5 SQMM CU | Nos. | 50 | 50 | 313 | 18 | N
91 | 85359090 | 3C x 2.5 SQMM CU | Nos. | 30 | 30 | 313 | 18 | N
92 |  | CABLE GLANDS
93 |  | Double compression stainless steel cable gland suitable for following XLPE, FRLS cable sizes & as per relevant IS for Indoor use.
94 | 85389000 | 3.5C x 240, Sqmm XLPE AL | Nos. | 12 | 12 | 1573 | 18 | N
95 | 85389000 | 4C X 25, Sqmm XLPE AL | Nos. | 10 | 10 | 695 | 18 | N
96 | 85389000 | 4C X 10, Sqmm XLPE AL | Nos. | 6 | 6 | 585 | 18 | N
97 | 85389000 | 4C X 2.5, Sqmm XLPE AL | Nos. | 10 | 10 | 476 | 18 | N
98 | 85389000 | 3C X 2.5, Sqmm XLPE AL | Nos. | 8 | 8 | 476 | 18 | N
99 | 85389000 | 2C X 2.5, Sqmm XLPE AL | Nos. | 10 | 10 | 454 | 18 | N
100 | 85389000 | 2C X 4, Sqmm XLPE AL | Nos. | 10 | 10 | 512 | 18 | N
101 | 85389000 | 2C X 16, Sqmm XLPE AL | Nos. | 10 | 10 | 454 | 18 | N
102 | 85389000 | 7C x 2.5 SQMM CU | Nos. | 6 | 6 | 347 | 18 | N
103 | 85389000 | 3C x 2.5 SQMM CU | Nos. | 10 | 10 | 312 | 18 | N
104 |  | Cable Trays
105 |  | Ladder type FRP cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161 along with the 90 deg Horizontal Bend Ladder type, TEE Connection Ladder type, 90 deg Vertical Bend (inside) Ladder, 90 deg Vertical Bend (outside).
106 | 70080090 | 150mm Wide | m | 600 | 600 | 2041 | 18 | N
107 | 70080090 | 50mm Wide | m | 50 | 50 | 1534 | 18 | N
108 |  | Perforated type FRP cable tray (100mmx2mm, 3 Meter length) with minimum hot dip zinc coating 75 micron with accessories like coupler plates,bends, Stainless steels hardwares like nuts & bolts , bends, washers etc and as per IS & ES:8161 along with the 90 deg Horizontal Bend Perforated type, TEE Connection Perforated type, 90 deg Vertical Bend (inside) Perforated, 90 deg Vertical Bend (outside).
109 | 70080090 | 150mm Wide | m | 600 | 600 | 1534 | 18 | N
110 | 70080090 | 50mm Wide | m | 50 | 50 | 892 | 18 | N
111 |  | STEEL STRUCTURAL/ MS PLATE/ MS CHEQUARD PLATE
112 | 73081000 | ISA 50X50X6 | Ton | 2 | 2 | 219480 | 18 | N
113 | 73081000 | 3mm to 10mm thick MS plate conforming to IS-2062 | Ton | 0.8 | 0.8 | 256060 | 18 | N
114 | 73081000 | AnchorFastener | Nos | 1600 | 1600 | 219 | 18 | N
115 | 73081000 | Laying of cables in directly buried including supply of sand & bricks including sand filling & brick works after cable laying for directly burried & in trenches etc as per cabling layouts | m | 300 | 300 | 2124 | 18 | N
116 |  | EARTHING & LIGHTNING
117 |  | Hot dip Galvanized earthing and lightning protection materials along with the accessories conforming to IS (Galvanisation is 910gms/sq. mtr)
118 | 85354010 | 50 x 6 mm Copper Strip | m | 550 | 550 | 3894 | 18 | N
119 | 85354010 | 32 x 6 mm Copper Strip | m | 150 | 150 | 2761 | 18 | N
120 | 85354010 | 25 x 3 mm Copper Strip | m | 446 | 446 | 1062 | 18 | N
121 | 85354010 | 35x 6 mm GI Strip | m | 160 | 160 | 1274 | 18 | N
122 | 85354010 | 1C x 150mm2 PVC (Cu) cable Green colour | m | 186 | 186 | 1841 | 18 | N
123 | 85354010 | 1C x 35 mm2 PVC (Cu) cable Green colour | m | 60 | 60 | 590 | 18 | N
124 | 85354010 | 1C x 16 mm2 PVC (Cu) cable Green colour | m | 25 | 25 | 382 | 18 | N
125 | 85354010 | CABLE TRAY – 20 X 3 GI (2 RUNS) | m | 1200 | 1200 | 295 | 18 | N
126 | 85354010 | Hot dip Galvanized 10 Holes ∅13mm ground plate 550mmx50mmx6mm earth connection bar with fixing materials/ accessories , SS hardware etc. (min. coating 120 microns of zinc). | Nos | 10 | 10 | 1829 | 18 | N
127 | 85371000 | Earthing Lug
128 | 85371000 | 1C x 150mm2 PVC (Cu) cable Green colour | Nos | 8 | 8 | 83 | 18 | N
129 | 85371000 | 1C x 35 mm2 PVC (Cu) cable Green colour | Nos | 8 | 8 | 26 | 18 | N
130 | 85371000 | 1C x 16 mm2 PVC (Cu) cable Green colour | Nos | 4 | 4 | 31 | 18 | N
131 | 85371000 | SQUARE TAPE CLAMP | Nos | 25 | 25 | 218 | 18 | N
132 | 85371000 | TEST LINK | Nos | 8 | 8 | 1558 | 18 | N
133 | 85371000 | TAPE CLIP | Nos | 415 | 415 | 137 | 18 | N
134 | 85371000 | TEE JOINT | Nos | 50 | 50 | 271 | 18 | N
135 | 85371000 | Pile earthing: Pile earthing including all parts including required hardware and accessories
136 | 85371000 | Body Earth pit | Nos | 4 | 4 | 10060 | 18 | N
137 | 85371000 | Lightning Earth pit | Nos | 4 | 4 | 8779 | 18 | N
138 | 85371000 | Neutral Earth pit | Nos | 2 | 2 | 7682 | 18 | N
139 | 85371000 | Instrument earth pit | Nos | 2 | 2 | 7316 | 18 | N
140 |  | GENERAL SAFETY EQUIPMENT
141 | 40169100 | 3.3 kV, 900mm wide, electric grade floor rubber mat conforming to relevant IS. ISI mark shall be there on rubber mat. | m | 9 | 9 | 1369 | 18 | N
142 | 40169100 | 1.1 kV, 900mm wide, electric grade floor rubber mat (in pieces of length not less than 2 mtrs.) conforming to relevant IS. ISI mark shall be there on rubber mat. | m | 8 | 8 | 826 | 18 | N
143 | 40159030 | Rubber Hand Gloves of 3.3 KV grade. | Pairs | 2 | 2 | 1553 | 18 | N
144 | 40159030 | Rubber Hand Gloves of 415V grade. | Pairs | 2 | 2 | 2289 | 18 | N
145 | 30065000 | First aid box of GI, 18 SWG sheet with necessary items. | No. | 1 | 1 | 6402 | 18 | N
146 | 831000 | DANGER PLATE (As per IS 2551) | Nos. | 2 | 2 | 915 | 18 | N
147 | 5201 | CABLE ROUTE MARKER | Nos. | 25 | 25 | 549 | 18 | N
148 |  | Obtaining approval & arranging for inspection of complete installation from CEIG / Statutory Authority/local authority Jobs includes preparation of all required documents and necessary liasoning for getting approval. | LS | 1 | 1 | 365800 | 18 | N
149 |  | CONTROL & INSTRUMENTATION
150 |  | Supply of New Field Instruments
151 | 85371000 | PRESSURE SWITCH | Nos | 8 | 8 | 4024 | 18 | N
152 | 90268090 | PRESSURE TRANSMITTER | Nos | 9 | 9 | 8231 | 18 | N
153 | 84314390 | Orifice Plate | Nos | 1 | 1 | 3109 | 18 | N
154 |  | SUPPLY of New Control system
155 | 85371000 | FIRE PUMP CONTROLLER -FOR NEW MOTOR DRIVER JOCKEY PUMP-01 | No. | 1 | 1 | 466395 | 18 | N
156 | 85371000 | FIRE PUMP CONTROLLER -FOR NEW MOTOR DRIVER JOCKEY PUMP-02 | No. | 1 | 1 | 466395 | 18 | N
157 | 85371000 | FIRE PUMP CONTROLLER -FOR EXISTING MOTOR DRIVEN FIRE PUMP-01 | No. | 1 | 1 | 466395 | 18 | N
158 | 85371000 | FIRE PUMP CONTROLLER -FOR EXISTING DIESEL DRIVEN FIRE PUMP-01 | No. | 1 | 1 | 466395 | 18 | N
159 | 85371000 | FIRE PUMP CONTROLLER -FOR EXISTING DIESEL DRIVEN FIRE PUMP-02 | No. | 1 | 1 | 466395 | 18 | N
160 | 85371000 | FIRE PUMP CONTROLLER -FOR NEW DIESEL DRIVEN FIRE PUMP-03 | No. | 1 | 1 | 466395 | 18 | N
161 | 85371000 | FIRE PUMP CONTROLLER -FOR NEW DIESEL DRIVEN FIRE PUMP-04 | No. | 1 | 1 | 466395 | 18 | N
162 | 85311090 | NEW MIMIC/REPEATER PANEL IN NEW FWPH NEAR TCB | No. | 1 | 1 | 466395 | 18 | N
163 | 5201 | NEW AUTOMATION PLC PANEL FOR FIRE PUMP | No. | 1 | 1 | 3072720 | 18 | N
164 |  | Supply of New Instrument & Control Cables
165 | 90011000 | 24C SM FIBER OPTIC CABLE | Mtr | 6450 | 6450 | 153 | 18 | N
166 | 85389000 | RS-485 CABLE | Mtr | 1705 | 1705 | 183 | 18 | N
167 | 85444299 | 02CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | Mtr | 330 | 330 | 271 | 18 | N
168 | 85444299 | 06CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | Mtr | 1150 | 1150 | 555 | 18 | N
169 | 85444299 | 24CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | Mtr | 2190 | 2190 | 1711 | 18 | N
170 | 85444299 | 12CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | Mtr | 1720 | 1720 | 979 | 18 | N
171 | 85444299 | 03CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | Mtr | 640 | 640 | 342 | 18 | N
172 |  | Supply of New Erection Materials
173 | 73049000 | 1/2" X SCH.160 -A106 GR.B -Pipe Seamless B.36.10 | Nos. | 20 | 20 | 3351 | 18 | N
174 | 73072900 | 1/2" NPTM X 1/2" PE X SCH.160 -A106 GR.B -Pipe Nipple B.36.10 -100MM LG | Nos. | 10 | 10 | 183 | 18 | N
175 | 7307 | 3/4" NPTF X 1/2" SW 6000# -A105 -Reducing Coupling B.16.11 | Nos. | 10 | 10 | 366 | 18 | N
176 | 73072100 | 1/2" X SCH.160 300# -A105 -Flange S.W.R.F. 125 AARH B16.5 | Nos. | 20 | 20 | 512 | 18 | N
177 | 84841090 | 1/2" 300# SS304 SPWD 4.5 THK Graphite Filler with C.S. Outer Ring -Gasket Spiral wound B1.620 | Nos. | 10 | 10 | 146 | 18 | N
178 | 7318 | 1/2" UNC X 85 LG SA193 GRB7 & SA 194GR2H/CD Plated -FT Studs with 2 Nuts & 2 Washers | Nos. | 40 | 40 | 110 | 18 | N
179 | 848180 | 1/2" NPTF x 1/2" NPTF 6000# SS316 -Two way manifold | Nos. | 10 | 10 | 3198 | 18 | N
180 | 8536 | 1/2 "NPTM 6000# SS316 -Plug | Nos. | 10 | 10 | 348 | 18 | N
181 | 73072900 | 1/2" SW 3000# A105 -Equal Tee,B16.11 | Nos. | 10 | 10 | 348 | 18 | N
182 | 84818010 | 1/2" SW 800# A105 -Globe Valve,B16.11 | Nos. | 10 | 10 | 2100 | 18 | N
183 | 84818030 | 1/2" NPTF 3000# A105 -cap | Nos. | 10 | 10 | 330 | 18 | N
184 | 85369030 | Signal Junction Box (Blue): Flame Proof /Ex-Proof, Die Cast AL LM6 Body, 6 Inlet+2 Outlet. suitable for hazardous area of zone 1, group IIA/IIB, T3 ,having PESO/CMIFR approval. Complete in all respect accessories like Certified Flameproof /Exproof SS316 Double Compression cable glands with PVC shrouds & SS plugs for excess entries, SS 316 engraved Tag Plate, mounting clamp & SS 316 fasteners. | No. | 1 | 1 | 5393 | 18 | N
185 | 85369030 | Control Junction Box(Grey): Flame Proof /Ex-Proof, Die Cast AL LM6 Body, 12 Inlet+2 Outlet. suitable for hazardous area of zone 1, GROUP IIA/IIB, T3 or better having PESO/CMIFR approval. Complete in all respect accessories like certified Flameproof /Exproof SS316 Double Compression cable glands with PVC Shrouds & SS Plugs for excess entries, SS 316 engraved Tag Plate, mounting clamp & SS 316 fasteners. | No. | 1 | 1 | 7499 | 18 | N
186 | 73063010 | 2'' GI PIPE | Mtrs | 90 | 90 | 1770 | 18 | N
187 | 7216 | Structural Steel which includes angel Iron (75 X 75 X 6 mm. Thk. MS), Channel (100 X 50 X 6 mm Thk. M.S. As per IS-226), M.S. Plate (6 mm Thk. M.S.) & foundation Bolts & Nuts etc. For Inst. Pedestals (M 10 Φ X 100 mm Long, C.S. Galvanized As per IS). Structural Steel shall be used for CCTV installation on Periphery wall and wall mounting. | KG | 250 | 250 | 256 | 18 | N
188 |  | SUPPLY OF NEW CABLE GLANDS
189 | 90011000 | 24C SM FIBER OPTIC CABLE | NOS | 6 | 6 | 329 | 18 | N
190 | 85389000 | RS-485 CABLE | NOS | 28 | 28 | 274 | 18 | N
191 | 85444299 | 02CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | NOS | 22 | 22 | 366 | 18 | N
192 | 85444299 | 06CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | NOS | 30 | 30 | 649 | 18 | N
193 | 85444299 | 24CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | NOS | 38 | 38 | 826 | 18 | N
194 | 85444299 | 12CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | NOS | 22 | 22 | 732 | 18 | N
195 | 85444299 | 03CX2.5 MM2 (8X.02) FIRE SURVIVAL CABLE (FOR NOTIFICATION DEVICES RATING 3 HOURS) | NOS | 36 | 36 | 472 | 18 | N
196 |  | Supply of New Cables, Switches and Erection Material
197 | 85176990 | Layer 2 managed Industrial Grade Switch with 8 PORT POE+ 10/100/1000 MBPS BASE -T and PORT 4 1G SFP& IP 30 NEEMA TS -2 . | Nos. | 2 | 2 | 67673 | 18 | N
198 | 85444299 | CAT 6 cable.Acessories like Lugs, Adapter, Blank Plate & Patch Cord etc as required is included. | Lot. | 1 | 1 | 73160 | 18 | N
199 | 854449 | HDPE Duct for 24 core OFC armoured cable. | Mtrs | 6700 | 6700 | 178 | 18 | N