## Sheet1
BOQ Item Sr No(unique no - alphanumeric) | HSN / SAC Code (Numeric) | Item Description(Text) | Unit(Text) | Scheduled Qty(Numeric) | Design Qty(Numeric) | Rate Basic(Numeric) | GST %(Numeric) | Non-Scheduled(Yes/No)
1 | 8537 | Integration and Monitoring of Main RMU Panel through potential free contact which have 2 nos. SF6 type breakers and O/G 1 nos. along with all accessories for remote status monitoring. | Nos. | 3 | 3 | 41068.12 | 18 | N
2 | 85362010 | Automation of unmotorized LT ACB breaker--- Supply, Installation, Testing and Commissioning of spring charging motor, Under Voltage release, Shunt trip, closing coil, Key Interlock, Spring charge indication switch in Main LT Panel for monitoring of on/off status. The LT Panel which have Incoming 2 no's 1600 Amp ACBs, 1600A Bus coupler and 4 nos.1000 Amp outgoing ACBs along with Multifunction Meters with RS 485 port for automation of Switch Gear Panel. | Nos. | 7 | 7 | 155749.1 | 18 | N
3 | 85044090 | Integration of UPS System , Fire suppression system & DG system with Monitoring Panel of Building Management System. | Nos. | 2 | 2 | 43023.75 | 18 | N
4 | 85079090 | Integration & monitoring of Server, UPS, SCADA, Battery room--- Integration & monitoring of field sensors (Temp/RH Sensor) to be provided with suitable 0-10V or 4-20mA outputs for transmitters wherever applicable. Suitable housings to be considered as per application and location of sensors. Suitable Dry contacts to be provided in panels by panel vendors. In case of switches, suitable contacts to be provided by manufacturer for integration to BMS Controller (Server,UPS,SCADA and Battery Room) | Nos. | 6 | 6 | 13689.37 | 18 | N
5 | 85442090 | Laying of 4 core 1.5 sq mm Cu armoured BMS control cabling 1100 volt grade XLPE insulated FRLS PVC outer sheathed copper conductor armoured cable as per specification in existing trenches, cable trays duct, clamped to wall with suitable clamps, including fixing bolts, connecting testing and commissioning for controller to field devices. Testing and commissioning for controller to field devices. | Mtr. | 500 | 500 | 264.92 | 18 | N
7 | 853620 | 32 AMP industrial Male Female Plug and socket. | Nos. | 30 | 30 | 3584.79 | 18 | N
8 | 3917 | Supply and installation of UTP Cat 6 cable in 20 mm dia PVC conduits with all accessories loong with Network switch complete as required. | Mtr. | 200 | 200 | 173.76 | 18 | N
9 | 85362020 | Supply Installation Testing and Commissioning of 250/125 Amp Microprocessor based MCCB Ics=100%Icu 36 KA with control cabling including all accessories. | Nos. | 6 | 6 | 49698.95 | 18 | N
10 | 8517620003 | Supply, Installation, Testing & Commissioning of 4 port 10/100 network switch, 180W Power, IP multicast snooping, Data-driven IGMP support, Standard 802.1d Spanning Tree support, Support for IEEE 802.3ad Link Aggregation Control Protocol (LACP) I/C crimping, connections with standard accessories as required. | Nos. | 2 | 2 | 19165.12 | 18 | N
11 | 85287211 | Supply,Erection,testing & commissioning of 4U Wall Mount Rack, 2 port power socket, inbuilt Fan with Lock & Key with accessories. | Nos. | 1 | 1 | 13689.37 | 18 | N
12 | 8537 | Supply, installation, testing and commissioning of LT Panel suitable for 440V, 3 Phase, 4 Wire, 50 Hz Supply System (New DB) with PLC Logic with following equipment’s. | Set | 1 | 1 | 2347271.5
12-1 |  | For Transformer Incomer
| 85362010 | 2 Nos. of 440V, 800A 4P EDO ACB with inbuilt microprocessor-based O/L, S/C, E/F Relay with last 5 trip history & RS485 port for communication. | Nos. | 1 | 1 |  | 18 | N
12-2 |  | For DG Incomer
| 85362010 | 2 Nos. of 440V, 800A 4P EDO ACB with inbuilt microprocessor-based O/L, S/C, E/F Relay with last 5 trip history & RS485 port for communication. | Nos. | 1 | 1 |  | 18 | N
12-3 |  | Bus Coupler
| 85362010 | 1 No. of 440V, 800A 4P EDO ACB with inbuilt microprocessor-based O/L, S/C, E/F Relay with last 5 trip history & RS485 port for communication, mechanical interlock. | Nos. | 1 | 1 |  | 18 | N
12-4 |  | Busbar
| 853690 | 4 Pole Aluminum, colour coded bus bars suitable for 440V 50Hz (after derating) | Nos. | 1 | 1 |  | 18 | N
12-5 |  | Capacitor Bank
| 8532 | 150 KVAR Capacitor Bank suitable for 440V, 3 Phase, 50Hz Supply System | Nos. | 1 | 1 |  | 18 | N
13 |  | Main Distribution Panel | Set | 1 | 1 | 1179621.52
13-1 |  | Incomer
| 90303100 | 1 No. 440V 800Amp 4P MCCB with MFM & Indicator | Nos. | 1 | 1 |  | 18 | N
13-2 |  | Outgoing
| 85362020 | 8 Nos. of 440V 250A 4P MCCB with two square compartments | Nos. | 1 | 1 |  | 18 | N
13-3 |  | Bus coupler
| 85389000 | 440V 800A 4P MCCB with mechanical interlock | Nos. | 1 | 1 |  | 18 | N
14 |  | LT Distribution Panel | Set | 2 | 2 | 323330
14-1 |  | Incomer
| 85362020 | 440V 250A 4P MCCB with MFM Meter | Nos. | 1 | 1 |  | 18 | N
14-2 |  | Outgoing
| 85362020 | 10 Nos. 63Amp 4P MCCB | Nos. | 1 | 1 |  | 18 | N
15 |  | LT Cable
| 85442090 | Supply, laying, testing & termination of 1.1KV grade XLPE Al conductor armoured cable with suitable clamps, saddles, fixing bolts. | Nos. | 1 | 1
15-1 | 85446090 | 3.5 Core 300 sq. mm. | RM | 100 | 100 | 1647.94 | 18 | N
15-2 | 85446090 | 3.5 Core 120 sq. mm. | RM | 50 | 50 | 1381.97 | 18 | N
16 |  | Earthing | Set
16-1 | 8538 | Supply and installation of maintenance free earthing with chemical earthing pit with all necessary material. | No. | 2 | 2 | 16166.5 | 18 | N
16-2 | 85389000 | Supply & laying G.I. strip below ground/surface as strip earth electrode including connection/ termination with G.I. nut, bolt, spring washer etc. | No. | 2 | 2 |  | 18 | N
| 85389000 | 25mm X 6mm | Mtr. | 40 | 40 | 599.72 | 18 | N
17 |  | LT Termination
| 85442090 | Supply and cable end termination of the following XLPE Aluminum conductor armoured cable of 1.1KV grade including supply and fixing of crimping lugs, double compression glands with earthing
17-1 | 85446090 | 3.5 Core 300 sq. mm. | No. | 10 | 10 | 3859.1 | 18 | N
17-2 | 85446090 | 3.5 Core 120 sq. mm. | No. | 6 | 6 | 2816.1 | 18 | N
18 |  | Miscellaneous items | No. | Lum p- sum | Lum p- sum |  | 18 | N
Total