## Sheet1
BOQ Item Sr No(unique no - alphanumeric) | HSN / SAC Code (Numeric) | Item Description(Text) | Unit(Text) | Scheduled Qty(Numeric) | Design Qty(Numeric) | Rate Basic(Numeric) | GST %(Numeric) | Non-Scheduled(Yes/No)
1 | 853720 | Integration and Monitoring of Main RMU Panel through potential I free contact which have 2 no's SF6 type breakers and O/G 1 no's along with all accessories for remote status monitoring. | Nos | 2 | 0 | 41111.83 | 18 | N
2 | 85371000 | Supply Installation Testing and Commissioning of spring charging mator, Under Voltage release, Shunt trip, closing coil, Key Interlock, Spring charge indication switch in Main LT Panel for monitoring of on/off status. The LT Panel which have I/C 2 no's 1600 Amp ACB incomer & 1600A Buscopler O/G 1000 Amp 4 nos. ACB along with Multifunction Meters with RS 485 port for automation of Switch Gear Panel. | Nos | 7 | 0 | 155914.86 | 18 | N
3 | 85362020 | Supply Installation Testing and Commissioning of 250/125 Amp Microprocessor based MCCB Ices=100%Icu 36 KA with control cabling including all accessories. | Nos | 6 | 0 | 49751.84 | 18 | N
4 | 85079090 | Integration of UPS System with BMS Panel for Monitoring. | Nos | 2 | 0 | 43069.54 | 18 | N
5 | 84129090 | Integration and monitoring of Field sensors (Temp/RH Sensor) to be provided with suitable 0-10V or 4-20mA outputs for transmitters wherever applicable. Suitable housings to be considered as per application and location of sensors. Suitable Dry contacts to be provided in panels by panel vendors. Incase of switches suitable contacts to be provided by manufacturer for Integration to DDC (Server, UPS, Scada and Battery Room) | Nos | 6 | 0 | 13703.94 | 18 | N
6 | 85369090 | Supply and Installation of of 32 AMP Industrial Male Female Plug and socket. | Nos | 30 | 0 | 3588.61 | 18 | N
7 | 85442090 | Supply installation, laying of 4 core 1.5 sqmm Cu armoured BMS control cabling 1100 volt grade XLPE insulated FRLS PVC outer sheathed copper conductor armoured cable as per specification In existing trenches, cable trays ducts, clamped to wall with suitable clamps, including fixing bolts, connecting testing and commissioning for controller to field devices. | Mtr | 500 | 0 | 265.2 | 18 | N
8 | 85444299 | Supply and installation of UTP Cat 6 cable in 20 mm dia PVC conduits with all accessories long with Network switch complete as required. | Mtr | 200 | 0 | 174.01 | 18 | N
9 | 85365090 | Supply, Installation, Testing & Commissioning of 4 port 10/100 network switch, 180W Power, IP multicast snooping, Data-driven IGMP support, Standard 802.1d Spanning Tree support, Support for IEEE 802.3ad Link Aggregation Control Protocol (LACP) i/c crimping, connections with standard accessories as required. | Nos | 2 | 0 | 19185.52 | 18 | N
10 | 847330 | Supplying, erecting, testing & commissioning of 4U Wall Mount Rack, 2 port power socket, inbuilt Fan with Lock & Key with accessories of standard make etc. | Nos | 1 | 0 | 13703.94 | 18 | N
11 |  | ELECTRICAL REDUNDANCY SYSTEM
12 | 85381090 | Supply, Installation, testing and commissioning of LT Panel suitable for 440V, 3 Phase, 4 Wire, 50 Hz Supply System (New DB) with PLC Logic with following equipment's | Set | 1 | 0 | 2349769.56 | 18 | N
13 |  | For Transformer Incomer
14 | 85362010 | 2 Nos. of 440V, 800A 4P EDO ACB with inbullt microprocessor based O/L, S/C, E/F Relay with last 5 trip history & RS485 port for communication.
15 |  | For DG Incomer
16 | 85362010 | 2 Nos. of 440V, 800A 4P EDO ACB with inbuilt microprocessor based O/L, S/C, E/F Relay with last 5 trip history & RS485 port for communication.
17 |  | Buscoupler
18 | 85362010 | 1 No. of 440V, 800A 4P EDO ACB with inbuilt microprocessor based O/L, S/C, E/F Relay with last 5 trip history & RS485 port for communication, mechanical interlock
19 |  | Busbar
20 | 76169990 | 4 Pole Aluminium, colour coded bus bars suitable for 440V 50Hz (after derating)
21 |  | Capacitor Bank
22 | 85321000 | 150 KVAR Capacitor Bank suitable for 440V, 3 Phase, 50Hz Supply System
23 | 8537 | Main Distribution Panel | Set | 1 | 0 | 1180876.92 | 18 | N
24 |  | Incomer
25 | 8537 | 1 No. 440V 800Amp 4P MCCB with MFM & Indicator
26 |  | Outgoing
27 | 8537 | 8 Nos. of 440V 250A 4P MCCB with two square compartments
28 |  | Buscoupler
29 | 8537 | 440V 800A 4P MCCB with mechanical interlock
30 | 85381090 | LT Distribution Panel | Set | 2 | 0 | 323674.1 | 18 | N
31 |  | Incomer
32 | 85381090 | 440V 800A 4P MCCB with mechanical interlock
33 |  | Outgoing
34 | 85381090 | 10 Nos. 63Amp 4P MCCB
35 | 85442090 | LT Cable
36 | 85442090 | Supply, laying, testing & termination of 1.1KV grade XLPE AI conductor armoured cable with suitable clamps, saddles, fixing balts.
37 | 85442090 | 3.5 Core 300 sq. mm. | RM | 100 | 0 | 1649.69 | 18 | N
38 | 85442090 | 3.5 Core 120 sq. mm. | RM | 50 | 0 | 1383.45 | 18 | N
39 |  | Earthing
40 | 72159090 | Supply and installation of maintenance free earthling with chemical earthling pit with all necessary material. | Set | 2 | 0 | 16183.71 | 18 | N
41 | 85389000 | Supply & laying G.I. strip below ground/surface as strip earth electrode including connection/termination with G.I. nut, bolt, spring washer etc.
42 | 85389000 | 25mm X 6mm | Meter | 40 | 0 | 600.36 | 18 | N
43 |  | LT Termination
44 | 85442090 | Supply and cable end termination of the following XLPE Aluminium conductor armoured cable of 1.1KV grade Including supply and fixing of crimping lugs, double compression glands with earthling
45 | 85442090 | 3.5 Core 300 sq. mm. | No. | 10 | 0 | 3863.21 | 18 | N
46 | 85442090 | 3.5 Core 120 sq. mm. | No. | 6 | 0 | 2819.1 | 18 | N