## Sheet1
BOQ Item Sr No(unique no - alphanumeric) | HSN / SAC Code (Numeric) | Item Description(Text) | Unit(Text) | Scheduled Qty(Numeric) | Design Qty(Numeric) | Rate Basic(Numeric) | GST %(Numeric) | Non-Scheduled(Yes/No)
1 | 85312000 | Supply of single Loop Analog addressable Fire Alarm system with loop the panel shall have a built in power supply and battery charger. RDSO Spec. No.RDSO/SPN/217/2018 Ver.2.0 or latest. | Nos | 7 | 7 | 87500 | 12 | N
2 | 85311020 | Supply of Multi Sensor detector Dual Optical/Thermal with rotatries and back boxes including base. RDSO Spec. No.RDSO/SPN/217/2018 Ver.2.0 or latest. | Nos | 105 | 107 | 2946.4286 | 12 | N
3 | 85319000 | Supply Installation Testing and Commissioning of aspiration type smoke detector. Highly sensitive smoke aspiration system for monitoring of rooms and equipment's for earliest possible fire detection For Relay rooms | Nos | 7 | 7 | 223214.2857 | 12 | N
4 | 85311020 | Supply of Addressable Single action indoor manual call point with back box(RED) and also including key. RDSO Spec. No.RDSO/SPN/217/2018 Ver.2.0 or latest. | Nos | 7 | 29 | 3120 | 12 | N
5 | 85311020 | Supply of Sounder having range of 81 dbA to 92 dbA. RDSO Spec. No.RDSO/SPN/217/2018 Ver.2.0 or latest. | Nos | 14 | 29 | 2760 | 12 | N
6 | 85311020 | Supply of Intelligent addressable Output module having facility to activate sounders etc. RDSO Spec. No.RDSO/SPN/217/2018 Ver.2.0 or latest. | Nos | 14 | 14 | 2700 | 12 | N
7 | 85311020 | Supply of Intelligent addressable input module for monitoring purpose. RDSO Spec. No.RDSO/SPN/217/2018 Ver.2.0 or latest. | Nos | 28 | 28 | 2700 | 12 | N
8 | 73110030 | Design and supply of 100Ltrs Cylinder with valve and warning sign boards.[Make: siemens or ansul or similar specifications, product should be Underwriters Laboratories(UL) listed.] RDSO Spec. No. RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 7 | 11 | 111607.1429 | 12 | N
9 | 73110030 | Design and supply of 67.5Ltrs Cylinder with valve and warning sign boards.[Make: sinorix 1230 or ansul or similar specifications, product should be UL listed RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 7 | 7 | 91920 | 12 | N
10 | 2914 | Supply of 3M Novec 1230/ FK-5-1-12 Fire Protection fluid factory fill in the above cylinders RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 1350 | 1350 | 2460 | 12 | N
11 | 85059000 | Supply of Master Cylinder Accessories listed below specifications, product should be Underwriters Laboratories(UL) listed.] includes a. Pr.Guage + Low Pr.Supervisory Switch b. Electromagnetic Actuator c. Manual Actuator d.Pneumatic Actuator e. Flexible Discharge Hose f. Flexible Actuation Hose g. Tee As per RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 7 | 7 | 58035.7143 | 12 | N
12 | 85059000 | Supply of End Slave Cylinder Accessories listed below [Make: siemens or ansul or similar specifications, product should be Underwriters Laboratories (UL) listed.] a. Pr. Guage + Low Pr. Supervisory Switch b. Electromagnetic Actuator c. Flexible Discharge Hose d. Flexible Actuation Hose e. Tee g. Elbow As per RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 7 | 8 | 33928.5714 | 12 | N
13 | 84818090 | Supply of check valve [Make: siemens or ansul or similar specifications, product should be UL approved.] as per RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 14 | 14 | 19800 | 12 | N
14 | 74199990 | Supply of discharge Nozzles [Make: siemens or ansul or similar specifications, product should be UL approved.]as per RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 28 | 28 | 5357.1429 | 12 | N
15 | 85365090 | Supply of pressure switch suitable to above cylinders. as per RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 14 | 14 | 19200 | 12 | N
16 | 2914 | Gas Release panel with battery back up. as per RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 7 | 7 | 31250 | 12 | N
17 | 85072000 | Supply of manual Abort switch suitable to above cylinders. as per RDSO/SPN/218/2016 Ver.1.0 df2 or latest | Nos | 7 | 7 | 1800 | 12 | N
18 | 85312000 | Supply of manual release switch to cylinders. as per RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 7 | 7 | 1800 | 12 | N
19 | 73041910 | Supply of schedule 40 seamless Pipes as per ASTM A 106, Gr. B, Sch 40, with Fittings confirming to ASTM A 105, Sch 40. including pipe supports, painting, etc. for the protected room up to the cylinder banks, this includes for relay & power room.[make :TATA or Jindal or similar]. as per RDSO/SPN/218/2016 Ver.1.0 df2 or latest. | Nos | 7 | 7 | 71428.5714 | 12 | N
20 | 85442090 | Supply of unaromed Fire Survival circuit integrity cable ( inside Only) | Nos | 1100 | 1200 | 156 | 12 | N
21 | 8544 | Supply of 2cx1.5 sq mm shielded ATC frls armoured cables.[product should ISI marked] | Nos | 1000 | 1100 | 72 | 12 | N
22 | 73110090 | Gas Manifold for two cylinders made of sch 40 seamless pipe with required couplings, end cap, etc.[make :TATA or Jindal or similar]. | Nos | 7 | 7 | 16071.4286 | 12 | N
23 | 85319000 | Supply, Installation of Air sampling CPVC Pipes with all required accessories | Nos | 7 | 7 | 16071.4286 | 12 | N
24 | 85319000 | Supervision, programming , testing & Commissioning charges for Aspiration smoke detection | Nos | 7 | 7 | 0 | 12 | N
25 | 85312000 | Installation ,Testing & commissioning of Fire Alarm System | Nos | 7 | 9 | 16071.4286 | 12 | N
26 | 73110030 | Installation ,Testing & commissioning of fire Suppression System | Nos | 7 | 9 | 16071.4286 | 12 | N