## Sheet1
BOQ Item Sr No(unique no - alphanumeric) | HSN / SAC Code (Numeric) | Item Description(Text) | Unit(Text) | Scheduled Qty(Numeric) | Design Qty(Numeric) | Rate Basic(Numeric) | GST %(Numeric) | Non-Scheduled(Yes/No)
1 | 5201 | Supply of Fire Fighting Application MS Hose Box to keep two number of hoses and 1 No. of branch pipe with nozzle having proper glass window type double door with universe open key, painted inside white and outside Post Office Red, near every hydrant point including conveyance, all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specifications and as directed by the Departmental Officers. Make: (Make: OMEX/ KARTAR/ SAFE GUARD/ Equivalent) | Numbers | 37 | 0 | 5168 | 18 | N
2 | 59090020 | Supply and fixing Hose Tray to accommodate 15 metre RRL Hose 2 Nos. and Branch pipe in Fire Duct as directed by the Departmental Officers. | Numbers | 45 | 0 | 2120.4 | 18 | N
3 | 7306 | Wrapping and coating anti-corrosive treatment for the following under ground MS pipe having one coat of anticorrosive metal primer, one layer of asphalt tar tape wound over th MS pipe as per standard methods as per standard specifications and as directed by the Departmental Officers. 150mm dia. Wrapping and coating | Running Metre | 120 | 0 | 304 | 18 | N
4 | 8481 | Supply, erection, testing and commissioning of following sizes of Heavy Duty Foot Valve including all accessories such as MS flange of table E gaskets, bolts & Nuts etc installed at end of 150/200 mm dia. Suction pipe line at sump including conveyance, all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: NORMEX/ KARTAR/Equivalent) 150mm dia. Heavy Duty Foot Valve at Pump Room | Numbers | 7 | 0 | 21014 | 18 | N
5 | 8481 | Supply, erection, testing and commissioning of following sizes of Heavy Duty Foot Valve including all accessories such as MS flange of table E gaskets, bolts & Nuts etc installed at end of 150/200 mm dia. Suction pipe line at sump including conveyance, all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: NORMEX/ KARTAR/Equivalent) 80mm dia. Heavy Duty Foot Valve at Pump Room | Numbers | 13 | 0 | 6297.55 | 18 | N
6 | 5201 | Supply and providing 1000 Litres capacity Priming Tank made up of PVC Make: SINTEX/ Equivalent | Numbers | 1 | 0 | 16720 | 18 | N
7 | 5201 | Priming Tank mounted with the Supporting Arrangement fabricated using MS Angle for the height of 3 metres from the floor level, inlet, outlet and drain arrangements inside the fire fighting pump room as directed by the Departmental Officers. | Numbers | 1 | 0 | 23935.25 | 18 | N
8 | 8544 | Supply and laying of following sizes of Armoured Aluminium/Copper cables for electrical motor, control panel, pressure switch, jockey motor etc., all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: POLYCAB/ PARAGON/ FINOLEX/ Equivalent) 4 core 250 sq.mm Armoured Aluminium cable | Running Metre | 100 | 0 | 2707.5 | 18 | N
9 | 8544 | Supply and laying of following sizes of Armoured Aluminium/Copper cables for electrical motor, control panel, pressure switch, jockey motor etc., all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: POLYCAB/ PARAGON/ FINOLEX/ Equivalent) 3 core 10 sq.mm Armoured Copper cable | Running Metre | 80 | 0 | 494 | 18 | N
10 | 8544 | Supply and laying of following sizes of Armoured Aluminium/Copper cables for electrical motor, control panel, pressure switch, jockey motor etc., all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: POLYCAB/ PARAGON/ FINOLEX/ Equivalent) 10 core 2.5 sq.mm Armoured Copper cable | Running Metre | 30 | 0 | 450.3 | 18 | N
11 | 8544 | Supply and laying of following sizes of Armoured Aluminium/Copper cables for electrical motor, control panel, pressure switch, jockey motor etc., all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: POLYCAB/ PARAGON/ FINOLEX/ Equivalent) 2 core 2.5 sq.mm Armoured Copper cable | Running Metre | 60 | 0 | 126.35 | 18 | N
12 | 8544 | Supply and laying of following sizes of Armoured Aluminium/Copper cables for electrical motor, control panel, pressure switch, jockey motor etc., all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: POLYCAB/ PARAGON/ FINOLEX/ Equivalent) 4 core 95 sq.mm Armoured Aluminium cable | Running Metre | 240 | 0 | 701.1 | 18 | N
13 | 8544 | Supply and laying of following sizes of Armoured Aluminium/Copper cables for electrical motor, control panel, pressure switch, jockey motor etc., all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: POLYCAB/ PARAGON/ FINOLEX/ Equivalent) 3 core 25 sq.mm Armoured Aluminium cable | Running Metre | 135 | 0 | 1235 | 18 | N
14 | 8544 | Supply and laying of following sizes of Armoured Aluminium/Copper cables for electrical motor, control panel, pressure switch, jockey motor etc., all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: POLYCAB/ PARAGON/ FINOLEX/ Equivalent) 2 core 2.5 sq.mm Armoured Copper cable | Running Metre | 135 | 0 | 126.35 | 18 | N
15 | 8544 | Supply and laying of following sizes of Armoured Aluminium/Copper cables for electrical motor, control panel, pressure switch, jockey motor etc., all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specificationa nd as directed by the Departmental Officers. Make: (Make: POLYCAB/ PARAGON/ FINOLEX/ Equivalent) 1 core 6 sq.mm Flexible Copper cable | Running Metre | 135 | 0 | 332.5 | 18 | N
16 | 9026 | Supply, erection, testing and commissioning of Pressure Gauge with 0 to 14kg range of reputed make with necessary valve, milling thread MS coupling fixed at delivery pipe line in pump house to read the developing pressure including conveyance, all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specification and as directed by the Departmental Officers. Make: (Make: H-GURU/ ISI MAKE/ Equivalent) | Numbers | 12 | 0 | 874 | 18 | N
17 | 8424 | Supply and keeping in position of 9 litres capacity Fire Buckets of 4 Nos. with Bucket stand as per standard specifications and as directed by the Departmental Officers. | Numbers | 8 | 0 | 2432 | 18 | N
18 | 84818090 | Supply, erection, testing and commissioning of Air Release Valve of 20mm dia. So as to release airlock in 100mm dia MS pipe at top most wet riser including conveyance, all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specification and as directed by the Departmental Officers. | Numbers | 13 | 0 | 820.8 | 18 | N
19 | 995429 | Providing, fixing Pipe Supports from columns / wall or suspenders from roof slab to suit various dia. Of pipes made out of GI/ MS adjustable rods threaded for a sufficient length to adjust the height of support along with clamping arrangement for holding pipes of anchor fastening, arrangement design of hanger and should conform with specifications. 80mm dia Wall or Suspenders | Numbers | 397 | 0 | 476.9 | 18 | N
20 | 995429 | Providing, fixing Pipe Supports from columns / wall or suspenders from roof slab to suit various dia. Of pipes made out of GI/ MS adjustable rods threaded for a sufficient length to adjust the height of support along with clamping arrangement for holding pipes of anchor fastening, arrangement design of hanger and should conform with specifications. 65mm dia Wall or Suspenders | Numbers | 406 | 0 | 456 | 18 | N
21 | 995429 | Providing, fixing Pipe Supports from columns / wall or suspenders from roof slab to suit various dia. Of pipes made out of GI/ MS adjustable rods threaded for a sufficient length to adjust the height of support along with clamping arrangement for holding pipes of anchor fastening, arrangement design of hanger and should conform with specifications 50mm dia Wall or Suspenders | Numbers | 420 | 0 | 441.75 | 18 | N
22 | 995429 | Providing, fixing Pipe Supports from columns / wall or suspenders from roof slab to suit various dia. Of pipes made out of GI/ MS adjustable rods threaded for a sufficient length to adjust the height of support along with clamping arrangement for holding pipes of anchor fastening, arrangement design of hanger and should conform with specifications 25mm dia Wall or Supspenders | Numbers | 1371 | 0 | 114 | 18 | N
23 | 38130000 | Supply and fixing of stored pressure ABC (Mono Ammonium Phosphate) Powder Type of 6 Kg capacity as per IS:15683 with pressure gauge, discharge hose & control nozzle, wall mounting bracket, safety clip etc. including conveyance, all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specification and as directed by the Departmental Officers. Make: Omex/ Safety first/ Equivalent | Numbers | 248 | 0 | 2128 | 18 | N
24 | 84241000 | Supply and fixing Carbon-di-Oxide Gas Type 2 Kg capacity Fire Entinguisher as per New IS:15683, complete with control valve, discharge hose with horn, wall mounting bracket, safety clip etc. including conveyance, all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specification and as directed by the Departmental Officers. Make: Omex/ Safety first/ Equivalent | Numbers | 236 | 0 | 6080 | 18 | N
25 | 84241000 | Supply and keeping in position of Trolley Mounted Type 22.5 kg Carbon-di-Oxide Fire Entinguisher as per IS:15683, complete with control valve, gun metal cap, pressure gauge, operation sticker,discharge hose, mounting trolley with moving wheel, safety clip etc. including conveyance, all incidental charges, necessary scaffolding and re-doing the dismantled portions to its original condition wherever found necessary etc. complete as per standard specification and as directed by the Departmental Officers. Make: Omex/ Safety first/ Equivalent | Numbers | 6 | 0 | 26600 | 18 | N
26 | 853110 | Supply of Addressable intelligent fire alarm 4- Loop Panel which consists of display board which will have 160 character Display with Touch key pad, Mother board which will have CORTEX 32 Bit Processor, In built RS- 485 Networking circuit for peer to peer networking, Inbuilt USB 2.0 port for upload and download of configuration tools, Two inbuilt programmable inputs, Two inbuilt NACs and Three Programmable relays and 4 Loop Card Circuits, power supply board which will have SMPS fully protected board, which operates on 120 to 230 V AC A+/- 10% with 50/60 Hz, battery back up 24V DC with built-in charger, the panel have IP-50 rating Optional: for BMS integration MODBUS converter, Graphical software, Software for TCP/IP module, Provision for Auto dialler Approval UL Listed (Make: Ravel/ GST/ Apollo/ Honeywell/ Equivalent) | Numbers | 2 | 0 | 137750 | 18 | N
27 | 85318000 | Supply, installation, testing and commissioning of Loop Card which will have 254 devices of both detectors and modules in a single line circuit, SLC supports both Class A and Class B wiring Approval: (Make: Ravel/ GST/ Apollo/ Honeywell/ Equivalent) | Numbers | 10 | 0 | 30400 | 18 | N
28 | 85311020 | Supply and fixing of MONITOR MODULE suitable for 4 L o o p panel with built in software data with adopter complete set for external devices (Make: Ravel/ GST/ Apollo/ Honeywell/ Equivalent) | Numbers | 11 | 0 | 5320 | 18 | N
29 | 84669200 | Supply and fixing of RELAY MODULE suitable for 4 Loop panel with built in software data with adopter complete set for external devices (Make: Ravel/ GST/ Apollo/ Honeywell/ Equivalent) | Numbers | 13 | 0 | 5890 | 18 | N
30 | 85049090 | Supply and fixing of 5 Amps Capacity power Supply Unit suitable for 4 x 2 Loop control panel (Make: Ravel/ GST/ Apollo/ Honeywell/ Equivalent) | Numbers | 4 | 0 | 6460 | 18 | N
31 | 39172990 | Supply and installation of PVC Casing cap of size100x50mm similar to Crown or similar brand conforming to IS 9537(Pt.3):1983, thickness2.4mm(heavy) to conceal the25mm MS pipes on the wall surface as directed by Engineer-in-Charge. | Running Metre | 3600 | 0 | 156.75 | 18 | N
32 | 84814000 | Supply and fixing single headed internal hydrant valve with instantaneous Gunmetal / Stainless Steel coupling of 63mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type -A) with blank Gunmetal / Stainless Steel cap and chain as required: Single headed Stainless steel (18.9.2) | Set | 78 | 0 | 4942.4153 | 18 | N
33 | 8424 | Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red, conforming to IS 884 complete with the following as required. 30M (18.17.1) | Set | 41 | 0 | 6984.1102 | 18 | N
34 | 590900 | Supply, and fixing 63mm dia, 15m long RRL hose pipe with 63mm dia male and female coulings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required: Stainless Steel (Grade 304)(18.16.2) | Set | 156 | 0 | 3581.0169 | 18 | N
35 | 84248990 | Supply, and fixing 63mm dia gun metal short branch pipe with 20mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required: Stainless Steel (Grade 304) (18.18.2) | Numbers | 78 | 0 | 1338.0508 | 18 | N
36 | 84248990 | Providing, fixing, testing & commissioning of 15mm dia quartzoid bulb type sprinklers of rating 68 degree centigrade with required accessories: Pendent Sprinkler (18.21.1) | Each | 1076 | 0 | 420.2542 | 18 | N
37 | 84249000 | Providing, fixing, testing & commissioning of 15mm dia quartzoid bulb type sprinklers of rating 68 degree centigrade with required accessories: Horizontal Side wall Sprinkler (18.21.3) | Each | 1393 | 0 | 496.7373 | 18 | N
38 | 8424 | Providing, installation, testing & commissioning of adjustable rosette plate for 15mm dia in white finish UL listed or FM approved complete as required. (18.29) | Each | 1160 | 0 | 181.1441 | 18 | N
39 | 8307 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stock bar of following sizes complete as required. 1000mm (18.25.2) | Set | 1160 | 0 | 1270.4237 | 18 | N
40 | 84818090 | Providing, fixing , testing & commission of installation control valve of cast iron body, brass/bronze working parts comprising of water motor alarm, bronze seat clapper, clapper arm and hydraulically driven mechanical gong bell to sound continuous alarm emergency releases, stainer, pressure switch, cock valve complete with drain valve and bypass, test control box, ball valves, MS pipe of required size, flanges, orifice plate, gasket etc of following sizes as required 100MM dia (18.24.2) | Set | 4 | 0 | 36230.4237 | 18 | N
41 | 995429 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required: 200mm dia MS C Class Heavy Pipe (6.3mm thick)(18.7.9) | Metre | 13 | 0 | 4398.178 | 18 | N
42 | 995429 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required: 150mm dia MS C Class Heavy Pipe(18.7.8) | Metre | 2222 | 0 | 2877.3729 | 18 | N
43 | 995429 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required: 100mm dia MS C Class Heavy Pipe(18.7.7) | Metre | 508 | 0 | 2056.9915 | 18 | N
44 | 995429 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required: 80mm dia MS C Class Heavy Pipe(18.7.6) | Metre | 1030 | 0 | 1517.5847 | 18 | N
45 | 995429 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required: 65 mm dia MS C Class Heavy Pipe(18.7.5) | Metre | 978 | 0 | 1299.4068 | 18 | N
46 | 995429 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required: 50mm dia MS C Class Heavy Pipe(18.7.4) | Metre | 1093 | 0 | 1031.3136 | 18 | N
47 | 995429 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required: 25mm dia MS C Class Heavy Pipe(18.7.1) | Metre | 3568 | 0 | 598.9831 | 18 | N
48 | 84818030 | Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 780 of following sizes as required. 150mm dia Sluice Valve(18.12.6) | Set | 17 | 0 | 18325.339 | 18 | N
49 | 84818030 | Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 780 of following sizes as required. 100mm dia Sluice Valve(18.12.5) | Set | 9 | 0 | 11787.2458 | 18 | N
50 | 84818030 | Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 780 of following sizes as required. 80mm dia Sluice Valve at Sprinkler Header at Every Floor(18.12.4) | Set | 24 | 0 | 8611.1864 | 18 | N
51 | 84813000 | Supply, erection, testing and commissioning of Non- Return Valve of following sizes conforming to IS : 5312 complete with rubber gasket, GI bolts, nuts, washers etc as required: 150 mm dia NRV(18.14.7) | Set | 5 | 0 | 14319.2373 | 18 | N
52 | 84813000 | Supply, erection, testing and commissioning of Non- Return Valve of following sizes conforming to IS : 5312 complete with rubber gasket, GI bolts, nuts, washers etc as required: 100mm dia NRV (18.14.5) | Set | 1 | 0 | 8896.1864 | 18 | N
53 | 84818030 | Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 780 of following sizes as required: 50mm dia (18.12.2) | Set | 4 | 0 | 5802.2458 | 18 | N
54 | 84813000 | Supply, erection, testing and commissioning of Non- Return Valve of following sizes confirming to IS : 5312 complete with rubber gasket, GI bolts, nuts, washers etc as required: 50mm dia(18.14.2) | Set | 1 | 0 | 4661.4407 | 18 | N
55 | 7407 | Providing and fixing earth bus of 50mm x 5mm copper strip on surface for connections etc. as required (5.20) | Each | 1 | 0 | 5518.8559 | 18 | N
56 | 8413 | A) Supplying, installation, testing and commissioning of diesel engine driven main fire pump suitable for automatic operation and consisting of following, complete in all respects, as required: (Diesel Driven Pump) (B) Horizontal type, multistage, centrifugal pump of cast of iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. (C) Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant IS standard complete with auto starting mechanism, 12 /24 volts electric starting equipment, diesel tank, exhaust pipe extended upto 10 m outside pump house duly insulated with 50 mm thick glass wool with 1.0 mm thick aluminium sheet cladding, residential silencer, instruments and protection as per standard specification, stop solenoid for auto stop in the event of fault with audio indications, painted with post office red colour etc. as required. (D) MS fabricated, common base plate, coupling, coupling guard, foundation bolts etc. as required. (E) Suitable cement concrete foundation duly plastered and with anti- Vibration Pads 2850 LPM at 88M head(18.2.1) | Set | 1 | 0 | 551421.0593 | 18 | N
57 | 84138190 | A) Supplying, installation, testing and commissioning of Electric driven Main Fire Pump suitable for automatic operation and consisting of following, complete in all respects, as required: (B) Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. (C) Suitable HP Squirrel cage induction motor, TEFC, synchronous speed 1500 RPM, suitable for operation on 415 volts, 3 phase 50 Hz, AC supply with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS- 325. (D) M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. (E) Suitable cement concrete foundation duly plastered with anti vibration pads. 2850LPM at 88M Head (18.1.1) | Set | 2 | 0 | 364316.1441 | 18 | N
58 | 84138190 | (A) Supplying, installation, testing and commissioning of electric driven pressurisation pump suitable for automatic operation and consisting of following, complete in all respects, as required: (Jockey Pump) (B) Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS: 1520. (C) Suitable HP squirell cage induction motor TEFC type suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS: 325. (D) M.S.fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. (E) Suitable cement concrete foundation duly plastered and with anti vibration pads. 180LPM 88m head(18.3.1) | Set | 2 | 0 | 102364.9153 | 18 | N
59 | 8413 | (A) Supplying, installation, testing and commissioning of electric driven terrace pump suitable for automatic operation and consisting of following, complete in all respects, as required: (terrace Pump) (B) Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS: 1520. (C) Suitable HP squirell cage induction motor TEFC type suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS: 325. (D) M.S.fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. (E) Suitable cement concrete foundation duly plastered and with anti vibration pads. 900LPM at 35M Head(18.4.1) | Set | 1 | 0 | 82005.1271 | 18 | N
60 | 85362020 | INCOMING 800A, 50kA 4 Pole MCCB, Ics=100% Icu Rating Digital Voltmeter 0-500V with selector switch Ammeter (0-800 A) with selector switch & CTs etc. LED type RYB phase indicating lamps, ON, OFF, trip indicating Set of Copper Bus Bar 1000Amps OUTGOING (Note: All outgoing feeders for pumps should have digital Ammeter with selector switches, and LED type ON, OFF, trip indicating lamps) MAIN FIRE PUMP 250 Amp, 50kA TPN MCCB, Ics=100% Icu, with fully automatic Star/Delta starter suitable for 100 hp pump with overload protection, current sensing type single phase preventor complete with all accessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation. - 2 sets JOCKEY PUMP 125 Amp. 50kA TPN MCCB, Ics=100% Icu, with Suitable HP fully automatic Star/Delta starter with overload protection, current sensing type single phase preventor complete with all accessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation. - 2 sets DIESEL ENGINE CONTROL Control for diesel engine comprising - Automatic/Manual selector switch & 3 attempts starting device, timers and relays as required, push buttons, start/stop in manual mode Indicating lamp for high/ Low Lub. Oil pressure, High Water Temp and Engine on indication Battery charger suitable for 12V/24 V DC with boost and trickle selector switch, 0-30 V DC volt meter, and 0-20 A DC Ammeter(18.5.6) | Set | 1 | 0 | 463496.1441 | 18 | N
61 | 8481 | Supply and Fixing of fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap and chain as reqd for suitable dia MS pipe connection conforming to IS 904 as Required 4 way 150mm dia MS pipe(18.19.2) | Set | 3 | 0 | 11250.2542 | 18 | N
62 | 85319000 | Supplying , installation, testing & commissioning of intelligent analog addressable photothermal detector complete with mounting base complete as required. (17.2.4) | Each | 1102 | 0 | 2300.9322 | 18 | N
63 | 85319000 | Supply, installation, testing and commissioning of Addressable Manual Call Point as manual call point complete as required(17.2.14) | Each | 56 | 0 | 3116.4831 | 18 | N
64 | 8531 | Supply, installation, testing and commissioning of intelligent Addressable programmable sounder complete as required (17.2.6) | Each | 54 | 0 | 2134.2797 | 18 | N
65 | 85446090 | Supply and laying of 2 x 1.5 sqmm fire alarm armoured cable, 600/1000V rated with annealed copper conductor having XLPE insulation, steel wire armouring & FRLS outer sheath complete as required(17.5.2) | Metre | 11290 | 0 | 139.2797 | 18 | N
66 | 85319000 | Supply , installation, testing and commissioning of addressable Fire Control Module complete as required. (17.2.10) | Each | 14 | 0 | 2417.6695 | 18 | N
67 | 85319000 | Supply , installation, testing and commissioning of fault isolator complete with base as required(17.2.7) | Each | 49 | 0 | 2632.6271 | 18 | N
68 | 85311020 | Supply, installation, testing and commissioning of 6 zone voice alarm controller with USB, MP3 player (including 6 zone button paging station) with seamless integration facility with the main fire alarm panel for voice evaluation complete as required.(17.3.1) | Each | 13 | 0 | 101771.5678 | 18 | N
69 | 73089090 | Supply, installation, testing and commissioning of 1.5/3/6W metal box ceiling / wall speakers complete as required(17.3.3) | Each | 88 | 0 | 1443.5169 | 18 | N
70 | 8518 | Supply, installation, testing and commissioning of amplifier 75 watt, 25 V rms operating at 240 Volt AC supply complete as required(17.3.7) | Each | 5 | 0 | 117375.7203 | 18 | N
71 | 8517 | Supply, installation, testing and commissioning of Voice command keypad 6 zone command keypad 6 zone, with microphone assembly complete as required(17.3.9) | Each | 5 | 0 | 65820.5085 | 18 | N
72 | 8544 | Suppling and drawing of cable Fire Retardant PVC insulated copper conductor cable in the existing surface / recessed steel conduit of following pairs, cores and size including connections and interconnection etc., as required. Speaker cable Single pair, 2-core, 1.5 Sq mm (17.5.3.1) | Metre | 4720 | 0 | 43.4746 | 18 | N
73 | 85311020 | Supply, Installation, Testing and Commissioning of Central graphical fire Alarm management system to centrally monitor and operate the fire alarm system complete as required.(17.2.2) | Each | 2 | 0 | 161508.8559 | 18 | N
74 | 85311090 | Supply of Addressable fire alarm Repeater Panel with 320 character / Touch screen LCD display with inbuilt reset, acknowledge and silence switches complete as required.(17.2.3) | Each | 1 | 0 | 87503.0508 | 18 | N