## Sheet1
BOQ Item Sr No(unique no - alphanumeric) | HSN / SAC Code (Numeric) | Item Description(Text) | Unit(Text) | Scheduled Qty(Numeric) | Design Qty(Numeric) | Rate Basic(Numeric) | GST %(Numeric) | Non-Scheduled(Yes/No)
1 |  | 2
1 | 8537 | FIRE PUMPS (Positive Suction) :- Pumps shall be capable of furnishing not less than 150% of rated capacity at a head & Pump Efficiency should be of minimum 65% & The shut off head shall not exceed 120% of rated head Supplying, installing, testing and commissioning of electrical motor driven, end suction back pullout type centifugal, Positive Suction type, Main Fire Hydrant Pump capacity 2850 LPM at 140 Mtr Head coupled to Squirrel Cage Induction TEFC electrical motor The electric motor shall be of rated HP and speed and suitable for operation at 415V, 50Hz. The pump shall be of cast iron construction with bronze impeller, stainless steel shaft, flexible coupling and mechanical seal. The complete unit shall be mounted on a common structural steel base frame and shall include accessories such as foundation bolts, Vibration Isolators etc and as specified in the technical specifications. The Pump shall be UL Listed & FM Approved. Making cutout and RCC Inertia Block foundation which will hold the Antivibration spring/arrangement benith nibbed neoprene vibration isolation mounting of suitable size for installation of pumps cement concrete plaster (design, drawings and construction to be done by the Contractor) complete with anti-wbration arrangement and any additional structural reinforcment as required till finishing of the same.
2 |  | Cost of supply and delivery | Nos | 1 | 1 | 3039235 | 18 | N
3 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 1 | 1 | 139000 | 18 | N
4 | 8537 | FIRE PUMPS (Positive Suction) :- Pumps shall be capable of furnishing not less than 150% of rated capacity at a head & Pump Efficiency should be of minimum 65% & The shut off head shall not exceed 120% of rated head. Supplying, installing, testing and commissioning of electrical motor driven, end suction back pullout type centifugal, Positive Suction type, Main Fire Sprinkler Pump of capacity 2850 LPM at 140 Mtr Head coupled to Squirrel Cage Induction TEFC electrical motor. The electric motor shall be of rated HP and speed and suitable for operation at 415V, 50Hz. The pump shall be of cast iron construction with bronze impeller, stanless steel shaft, flexible coupling and mechanical seal. The complete unit shall be mounted on a common structuralsteel base frame and shall include accessories such as foundation bolts, Vibration Isolators etc and as specified in the technical specifications. The Pump shall be Ul. Listed & FMApproved. Making cutout and RCC Inertia Block foundation which will hold the Antsibration spring/arrangement benith ribbed neoprene vibration isolation mounting of suitable size for installation of pumps cement concrete plaster (design, drawings and construction to be done by the Contractor) complete with anti-vibration arrangement and any additional structural reinforcment as required til fishing of the same
5 |  | Cost of supply and delivery | Nos | 1 | 1 | 3039235 | 18 | N
6 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 1 | 1 | 139000 | 18 | N
7 | 8537 | FIRE PUMPS (Positive Suction) :- Pumps shall be capable of furnishing not less than 150% of rated capacity at a head & Pump Effciency should be of minimum 65% & The shut off head shall not exceed 120% of rated head. Supplying, installing testing and commissioning of electrical motor driven, end suction back pullout type centifugal Positive Suction type, Main Fire Drencher Pump of capacity 1550 LPM at 55 Mtr Head coupled to Squirrel Cage Induction TEFC electrical motor. The electric motor shall be of rated HP and speed and suitable for operation at 415V, 50Hz, The pump shall be of cast iron construction with bronze impeller, stainless steel shaft flexible coupling and mechanical seal. The complete unit shall be mounted on a common structural steel base frame and shall include accessories such as foundation bolts Vibration Isolators etc and as specified in the technical specifications The Pump shall be UL Listed & FM Approved. Making cutout and RCC Inertia Block foundation which will hold the Antivibration spring/arrangement benith ribbed neoprene vibration isolation mounting of suitable size for installation of pumps cement concrete plaster (design, drawings and construction to be done by the Contractor) complete with anti-vibration arrangement and any additional structural reinforcment as required till finishing of the same.
8 |  | Cost of supply and delivery | Nos | 1 | 1 | 1209300 | 18 | N
9 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 1 | 1 | 139000 | 18 | N
10 | 8537 | FIRE PUMPS (Positive Suction) :- Pumps shall be capable of furnishing not less than 150% of rated capacity at a head & Pump Effciency should be of minimum 65% & The shut off head shall not exceed 120% of rated head. Supplying, installing, testing and commissioning of electric motor driven, Positive end Suction type Vertical Inline Jockey Pump of capacity 180 LPM at 140 Mtr Head coupled to Squirrel Cage Induction TEFC electric motor of adequate HP and speed The electric motor shall be suitable for operation on 41V, 50Hz. The pump shall be centrifugal type of Stainless Steel construction with bronze impeller stainless steel shaft, flexstile coupling and mechanical seal The complete unit shall be mounted on a common structural steel base frame and shall include accessories such as foundation bolts, Vibration Isolators etc and as specified in the technical specifications. The Pump shall be UL Listed & FM Approved. Making cutout and RCC Inertia Block foundation which will hold the Antivibration springrarrangement benith ribbed neoprene vibration isolation mounting of suitable size for installation of pumps cement concrete plaster (design drawings and construction to be done by the Contractor) complete with anti-vibration arrangement and any additional structural reinforcment as required till finishing of the same
11 |  | Cost of supply and delivery | Nos | 2 | 2 | 731696 | 18 | N
12 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 2 | 2 | 69500 | 18 | N
13 | 8537 | FIRE PUMPS (Positive Suction) :- Pumps shall be capable of furnishing not less than 150% of rated capacity at a head & Pump Effciency should be of minimum 65% & The shut off head shall not exceed 120% of rated head. Supplying, installing, testing and commissioning of electric motor driven, Positive end Suction type Vertical Inline Jockey Pump of capacity 180 LPM at 55 Mtr Head coupled to Squirrel Cage Induction TEFC electric motor of adequate HP and speed The electric motor shall be suitable for operation on 41V, 50Hz. The pump shall be centrifugal type of Stainless Steel construction with bronze impeller stainless steel shaft, flexstile coupling and mechanical seal The complete unit shall be mounted on a common structural steel base frame and shall include accessories such as foundation bolts, Vibration Isolators etc and as specified in the technical specifications. The Pump shall be UL Listed & FM Approved. Making cutout and RCC Inertia Block foundation which will hold the Antivibration springrarrangement benith ribbed neoprene vibration isolation mounting of suitable size for installation of pumps cement concrete plaster (design drawings and construction to be done by the Contractor) complete with anti-vibration arrangement and any additional structural reinforcment as required till finishing of the same
14 |  | Cost of supply and delivery | Nos | 1 | 1 | 708900 | 18 | N
15 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 1 | 1 | 69500 | 18 | N
16 | 8537 | FIRE PUMPS (Positive Suction) :- Pumps shall be capable of fumishing not less than 150% of rated capacity at a head & Pump Effciency should be of minimum 65% & The shut off head shall not exceed 120% of rated head. Supplying, installing, testing and commissioning of Diesel Engine driven, suction back pullout type centifugal Standby Fire Hydrant/Sprinkler pump of capacity 2850 LPM at 140 Mtr Head coupled to diesel engine Pump shall be in accordance with IS-12469 The diesel engine shall be of rated BHP and speed. The pump shall be of cast iron construction with bronze impeller, stainless steel shaft, flexible coupling and mechanical seal. The complete unit shall be mounted on a common structural steel base frame and shall include accessories such as foundation bolts, casing relief valve, pressure relief valve etc and as specified in the technical specifications The rate shall be inclusive of loading, unloading, shifting for diesel engine, & SITC of diesel engine accessories such as fuel tank of suitable capacity for 6 hrs continuous operation, industrial grade muffler, pre-piped cooling system, instrument panel with tachometer, oil pressure gauges, battery for pump starting, etc and as specified in the technical specifications. Pump shall be postive suction (Stand by pump) The Pump shall be UL Listed & FM Approved Making cutout and RCC Inertia Block foundation which will hold the Antivibration spring/arrangement benith ribbed neoprene vibration isolation mounting of suitable size for installation of pumps cement concrete plaster (design, drawings and construction to be done by the Contractor) complete with anti-vibration arrangement and any additional structural reinforcment as required till finishing of the same.
17 |  | Cost of supply and delivery | Nos | 1 | 1 | 2599300 | 18 | N
18 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 1 | 1 | 139000 | 18 | N
19 |  | Design, manufacture, supply, installation, testing and commissioning of integrated, cubicle type, dead front, extensible sheet steel control panel anchoring the panel to the foundation. The panel shall be duly powder coated and suitable for 500 volts, 50 cycles, 4 wire supply Quoted price shall include 1100 volts grade rubber mats over 50mm thick teak wood platform, control wiring. The panel shall have separate compartments for bus bar and cable alleys. The Panel shall be as per enclosed Electrical SLD & Technical Specifications. Note: The panel should have provision for BMS compatibility.
20 |  | Cost of supply and delivery | Nos | 1 | 1 | 1390000 | 18 | N
21 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 1 | 1 | 41700 | 18 | N
22 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Main Hydrant Pump-30x95 Cu
23 |  | Cost of supply and delivery | Rmt | 40 | 40 | 4130 | 18 | N
24 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 40 | 40 | 306 | 18 | N
25 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Main Sprinkler Pump-30x95 Cu
26 |  | Cost of supply and delivery | Rmt | 40 | 40 | 4130 | 18 | N
27 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 40 | 40 | 306 | 18 | N
28 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Main Sprinkler Pump-30x95 Cu
29 |  | Cost of supply and delivery | Rmt | 40 | 40 | 1800 | 18 | N
30 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 40 | 40 | 175 | 18 | N
31 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Jockey Pump -1 - 4Cx 4 Cu
32 |  | Cost of supply and delivery | Rmt | 40 | 40 | 530 | 18 | N
33 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 40 | 40 | 100 | 18 | N
34 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Jockey Pump -2 - 4Cx 4 Cu
35 |  | Cost of supply and delivery | Rmt | 40 | 40 | 530 | 18 | N
36 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 40 | 40 | 100 | 18 | N
37 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Jockey Pump -3 - 4Cx 4 Cu
38 |  | Cost of supply and delivery | Rmt | 40 | 40 | 530 | 18 | N
39 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 40 | 40 | 100 | 18 | N
40 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Diesel Pump - 4Cx 4 Cu
41 |  | Cost of supply and delivery | Rmt | 20 | 20 | 530 | 18 | N
42 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 20 | 20 | 100 | 18 | N
43 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Booster Pump -1 - 4Cx 10 Cu
44 |  | Cost of supply and delivery | Rmt | 100 | 100 | 1140 | 18 | N
45 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 100 | 100 | 100 | 18 | N
46 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Booster Pump 2 - 4Cx 10 Cu
47 |  | Cost of supply and delivery | Rmt | 100 | 100 | 1140 | 18 | N
48 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 100 | 100 | 100 | 18 | N
49 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Booster Pump 3 - 4Cx 10 Cu
50 |  | Cost of supply and delivery | Rmt | 100 | 100 | 1140 | 18 | N
51 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 100 | 100 | 100 | 18 | N
52 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Booster Pump 4 - 4Cx 10 Cu
53 |  | Cost of supply and delivery | Rmt | 100 | 100 | 1140 | 18 | N
54 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 100 | 100 | 100 | 18 | N
55 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications LPDB - 4Cx 4 Cu
56 |  | Cost of supply and delivery | Rmt | 40 | 40 | 530 | 18 | N
57 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 40 | 40 | 100 | 18 | N
58 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications ELDB - 4Cx 4 Cu
59 |  | Cost of supply and delivery | Rmt | 40 | 40 | 530 | 18 | N
60 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 40 | 40 | 100 | 18 | N
61 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Fire Pump Panel - 3.5 C X 185 Cu
62 |  | Cost of supply and delivery | Rmt | 600 | 600 | 7506 | 18 | N
63 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 600 | 600 | 417 | 18 | N
64 | 8544 | Supply, Handling Laying proper connections testing and commissioning of following sizes of 1.1 KV grade FS XLPE insulated Armoured Copper conductor cables of sizes as below to be laid with necessary supports on provided cable trays/ on ceiling/wall as per site requirement in an approved manner complete as per technical specifications Dewatering Pump - 4Cx 4 Cu
65 |  | Cost of supply and delivery | Rmt | 20 | 20 | 530 | 18 | N
66 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Rmt | 20 | 20 | 76 | 18 | N
67 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Main Hydrant Pump 30x95 Cu
68 |  | Cost of supply and delivery | Nos | 4 | 4 | 2085 | 18 | N
69 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 4 | 4 | 834 | 18 | N
70 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Main Sprimkler Pump 30x95 Cu
71 |  | Cost of supply and delivery | Nos | 4 | 4 | 2085 | 18 | N
72 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 4 | 4 | 834 | 18 | N
73 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Main Drencher Pump - 4Cx16 cu
74 |  | Cost of supply and delivery | Nos | 4 | 4 | 834 | 18 | N
75 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 4 | 4 | 417 | 18 | N
76 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Jockey pump - 1 - 4Cx 4 cu
77 |  | Cost of supply and delivery | Nos | 4 | 4 | 530 | 18 | N
78 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 4 | 4 | 210 | 18 | N
79 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Jockey pump - 2 - 4Cx 4 cu
80 |  | Cost of supply and delivery | Nos | 4 | 4 | 417 | 18 | N
81 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 4 | 4 | 210 | 18 | N
82 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Jockey pump - 3 - 4Cx 4 cu
83 |  | Cost of supply and delivery | Nos | 4 | 4 | 417 | 18 | N
84 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 4 | 4 | 210 | 18 | N
85 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Diesel Pump - 4Cx 4 cu
86 |  | Cost of supply and delivery | Nos | 2 | 2 | 417 | 18 | N
87 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT. | Nos | 2 | 2 | 210 | 18 | N
88 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Booster Pump - 1 - 4cx 10 Cu
89 |  | Cost of supply and delivery | Nos | 2 | 2 | 695 | 18 | N
90 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 417 | 18 | N
91 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Booster Pump - 2 - 4cx 10 Cu
92 |  | Cost of supply and delivery | Nos | 2 | 2 | 695 | 18 | N
93 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 417 | 18 | N
94 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Booster Pump - 3 - 4cx 10 Cu
95 |  | Cost of supply and delivery | Nos | 2 | 2 | 695 | 18 | N
96 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 417 | 18 | N
97 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Booster Pump - 4 - 4cx 10 Cu
98 |  | Cost of supply and delivery | Nos | 2 | 2 | 695 | 18 | N
99 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 417 | 18 | N
100 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete LPDB - 4Cx 4 Cu
101 |  | Cost of supply and delivery | Nos | 2 | 2 | 417 | 18 | N
102 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 210 | 18 | N
103 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete ELDB - 4Cx 4 Cu
104 |  | Cost of supply and delivery | Nos | 2 | 2 | 417 | 18 | N
105 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 210 | 18 | N
106 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Fire Pump Panel - 3.5 C X 185 Cu
107 |  | Cost of supply and delivery | Nos | 8 | 8 | 305 | 18 | N
108 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 8 | 8 | 1112 | 18 | N
109 | 8544 | Providing & Installation of cable terminations for FS XLPE cables including Double compression type Brass glands and lugs(crimping type) and all accessories complete Dewatering Pump - 4Cx 4 Cu
110 |  | Cost of supply and delivery | Rmt | 2 | 2 | 530 | 18 | N
111 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 2 | 2 | 210 | 18 | N
112 | 73089090 | Supply and installation of sheet steel hot deep galvanised perforated type cable trays without cover manufactured from 16 SWG (16 mm thick) Gl sheet. The rate shall include bends, Tees, all supporting brackets, anchor fasteners, screws, bolts, nuts etc. including painting of cable trays. 50 × 50 mm wide tray - perforated
113 |  | Cost of supply and delivery | Rmt | 20 | 20 | 350 | 18 | N
114 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 20 | 20 | 100 | 18 | N
115 | 73089090 | Supply and installation of sheet steel hot deep galvanised perforated type cable trays without cover manufactured from 16 SWG (16 mm thick) Gl sheet. The rate shall include bends, Tees, all supporting brackets, anchor fasteners, screws, bolts, nuts etc. including painting of cable trays. 150 × 50 mm wide tray - perforated
116 |  | Cost of supply and delivery | Rmt | 100 | 100 | 570 | 18 | N
117 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 100 | 100 | 210 | 18 | N
118 | 73089090 | Supply and installation of sheet steel hot deep galvanised perforated type cable trays without cover manufactured from 16 SWG (16 mm thick) Gl sheet. The rate shall include bends, Tees, all supporting brackets, anchor fasteners, screws, bolts, nuts etc. including painting of cable trays. 300 × 50 mm wide tray - perforated
119 |  | Cost of supply and delivery | Rmt | 25 | 25 | 920 | 18 | N
120 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 25 | 25 | 278 | 18 | N
121 | 73089090 | Supply and installation of sheet steel hot deep galvanised perforated type cable trays without cover manufactured from 16 SWG (16 mm thick) Gl sheet. The rate shall include bends, Tees, all supporting brackets, anchor fasteners, screws, bolts, nuts etc. including painting of cable trays. 450 × 50 mm wide tray - perforated
122 |  | Cost of supply and delivery | Rmt | 15 | 15 | 1250 | 18 | N
123 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 15 | 15 | 350 | 18 | N
124 | 74091900 | Supply, Installation, testing & Commissioning of GI Earth strip including necessary accessories, clamping to walls, cable tray etc. as required 65 × 6 GI strip
125 |  | Cost of supply and delivery | Rmt | 80 | 80 | 370 | 18 | N
126 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 80 | 80 | 76 | 18 | N
127 | 74091900 | Supply, Installation, testing & Commissioning of GI Earth strip including necessary accessories, clamping to walls, cable tray etc. as required 32 × 6 GI strip
128 |  | Cost of supply and delivery | Rmt | 40 | 40 | 222 | 18 | N
129 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 40 | 40 | 62 | 18 | N
130 | 74091900 | Supply, Installation, testing & Commissioning of GI Earth strip including necessary accessories, clamping to walls, cable tray etc. as required 25 × 6 GI strip
131 |  | Cost of supply and delivery | Rmt | 40 | 40 | 174 | 18 | N
132 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 40 | 40 | 55 | 18 | N
133 | 74091900 | Supply, Installation, testing & Commissioning of GI Earth strip including necessary accessories, clamping to walls, cable tray etc. as required 25 × 6 GI strip
134 |  | Cost of supply and delivery | Rmt | 100 | 100 | 104 | 18 | N
135 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 100 | 100 | 49 | 18 | N
136 | 85362030 | Point Wiring Lighting & Power Point Provide all materials, accessories etc. for wiring of lights ceiling fans (If required), exhaust fans In MCB Control LPDB to first light point will be considered as primary light point and light to light looping will be considered as secondary light point Primary Point wiring & Secondary point Wiring using 3 x 25 sqmm and 3 x 1.5 sq.mm FRLS grade wires respectivty with ISI grade FRLSPVC (HMS) Conduit 25 mm ID Power circuit with 3x40 sq mm including supply and laying of conduits and its accessories concealed/surface over the slab/wall, surface mounted/ above false ceiling using PVC pull/junction boxes, light outlet boxes, Gi fan Boxes junction Boxes etc, including testing and commissioning complete The rate shall also include the cost of providing FRLS grade wires with ISI grade insulated copper conductor wire Conduit and accessories All wire ends shall be lugged property and ferruled at DB end The point wiring shall comply to 19732 (Cost of DB/MCB NOT to be included in this item as covered separately in below respective items) Contractor to refer Lighting looping Layouts and DB locations to calculate the average lengths for primary and secondary point. MCB Control : Primary Light Point with MCB control (Point wiring including from D.B. to Light Point)
137 |  | Cost of supply and delivery | Nos | 2 | 2 | 5212 | 18 | N
138 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 1740 | 18 | N
139 | 85362030 | Secondary Light point with MCB control (Point wiring include from Light Point to Light Point)
140 |  | Cost of supply and delivery | Nos | 4 | 4 | 4865 | 18 | N
141 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 4 | 4 | 1668 | 18 | N
142 | 85044090 | Primary Power Point (Point wiring include D B to First Light Point)
143 |  | Cost of supply and delivery | Nos | 4 | 4 | 3475 | 18 | N
144 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 4 | 4 | 1668 | 18 | N
145 | 85044090 | Secondary Power Point (Point wiring include from First Power Point to Secong Power Point)
146 |  | Cost of supply and delivery | Nos | 2 | 2 | 4865 | 18 | N
147 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 1668 | 18 | N
148 | 9405 | LIGHT FIXTURES Supply, Installation, testing & commissioning of light fixtures complete with: a) All fixing accessories mounting bracket. b) Earthing of fittings. 18W LED Light Fitting (T5)
149 |  | Cost of supply and delivery | Nos | 6 | 6 | 2085 | 18 | N
150 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 6 | 6 | 695 | 18 | N
151 |  | Supply, installation, testing & commissioning of Distribution Boards as per Given Specifications. a) Fabricated ready made. Double door, Lockable Powder coated MCBMCCBRCBOELCB as spected & shown on dương with b) Copper bustars together with tapped neutral bar fordul phases c) Copper sarth strip with tapping for EEC d) Interconnections and earthing e) Sheet steet enclosure suitable for recessed or surface mounting with hinged lockable doors antarocket with the incomer switch. f) Phase to phase isolation (PP) in case of Wh boards. g) Necessary support frame & painting, labeling, phase indicating lamps with fuses etc. complete. h) Brass glands for sending and receiving ends suitable for cable sizes mentioned in SLD. (Crimping luge forming part of the termination) i)Phase indication lamps j) Outgoing SP MCB should be D curve for Computer power circuit. k) Outgoing SP MCB should be C curve for power circuit. l) Outgoing SP MCB should be B curve for lighting circuit. m) The Distibution board should be sheet steel clad, wall/ recess mounting, dust and vermin proof distibution boards constructed with IK 08 for single door db & IK 09 for double door db & shall meet IP43 rating for indoor and IP54 for outdoor. n) The DB shall have appropriate no of top & Bottom for knokouts for outgoing circuits & shall be complete with necessary busbars, interconnection terminals & earth studs.all terminations in DB shall be complete with ferulling, dressing & all circuits & shall be properly labelled with PVC Strips having indentication as per the final approval of Consultant / Client (PMC Team).
152 | 85369090 | Supply , Installation , Testing and commissioning of Single door type SPN DB following as per specifications Incoming : 1 Nos RCBO (25A DP 100 mA) Outgoing : 4 Nos 10/16 A SP MCB (10 kA rating)
153 |  | Cost of supply and delivery | Nos | 1 | 1 | 10425 | 18 | N
154 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 1 | 1 | 2085 | 18 | N
155 | 85369090 | Supply , Installation , Testing and commissioning of Single door type SPN DB following as per specifications Incoming : 1 Nos RCBO (25A DP 100 mA) Outgoing : 6 Nos 10/16 A SP MCB (10 kA rating)
156 |  | Cost of supply and delivery | Nos | 1 | 1 | 10425 | 18 | N
157 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 1 | 1 | 2085 | 18 | N
158 | 8536 | Supply, Installation, testing & Commisioning of below specified 6/16 A sockets with 1.2 mm thick Gl back-boxes module plate and zinc passivated alongwith the necessary blank plates, Face-Plates etc as required complete with earthing, interconnections etc. Colour/Shade / all Type of switch-socket to be as per the Client/Architect/interior confirmation. Take Approval From Interior/ Architect on back Box and face plate Sizes. 6 / 16A stocket outlet.
159 |  | Cost of supply and delivery | Nos | 4 | 4 | 2780 | 18 | N
160 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 4 | 4 | 695 | 18 | N
161 | 84813000 | Supplying, installing, testing and commissioning of CI SWING CHECK TYPE NON RETURN VALVES (PN 25) as per IS 5312 with flanged ends drilled as per IS : 1538. Table-4&6. The valves shall be ISI marked. Rates shall be inclusive of galvanised bolts, nuts and washers and gaskets as specified in the technical specifications. The pressure rating of valve shall be as follows:
162 |  | Cost of supply and delivery
163 | 84813000 | 80 mm nominal dia ( PN 25 ) | Nos | 3 | 3 | 8540 | 18 | N
164 | 84813000 | 150 mm nominal dia ( PN 25 ) | Nos | 4 | 4 | 23510 | 18 | N
165 | 84813000 | 250 mm nominal dia ( PN25 ) | Nos | 1 | 1 | 71810 | 18 | N
166 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT
167 | 84813000 | 80 mm nominal dia ( PN 25 ) | Nos | 3 | 3 | 834 | 18 | N
168 | 84813000 | 150 mm nominal dia ( PN 25 ) | Nos | 4 | 4 | 1112 | 18 | N
169 | 84813000 | 250 mm nominal dia ( PN25 ) | Nos | 1 | 1 | 2780 | 18 | N
170 | 3917 | Supply, installation, testing & commissioning of Bronze BALL VALUE (PN 25) with fittings of screwed end type. 25 mm dia
171 |  | Cost of supply and delivery | Nos | 6 | 6 | 764 | 18 | N
172 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 6 | 6 | 556 | 18 | N
173 | 84818030 | Supplying, Installing, testing and commissioning Rising Spindle Type GATE VALVES (PN 10/PN 25) as per BS 1414 slim seal standared lever operated type with required flanges, nuts, bolts etc. complete (FOR PUMP SUCTION PN 10, PUMP DISCHARGE PN 25)
174 |  | Cost of supply and delivery
175 | 84818030 | 200 mm nominal dia (Tank outlet) | Nos | 3 | 3 | 48650 | 18 | N
176 | 84818030 | 200 mm nominal dia (Main pump Suction) | Nos | 4 | 4 | 48650 | 18 | N
177 | 84818030 | 150 mm nominal dia (Main pump Discharge) | Nos | 4 | 4 | 25715 | 18 | N
178 | 84818030 | 100 mm nominal dia (Jockey pump Suction) | Nos | 3 | 3 | 15290 | 18 | N
179 | 84818030 | 80 mm nominal dia (Jockey pump Discharge) | Nos | 3 | 3 | 10150 | 18 | N
180 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT
181 | 84818030 | 200 mm nominal dia (Tank outlet) | Nos | 3 | 3 | 2224 | 18 | N
182 | 84818030 | 200 mm nominal dia (Main pump Suction) | Nos | 4 | 4 | 2224 | 18 | N
183 | 84818030 | 150 mm nominal dia (Main pump Discharge) | Nos | 4 | 4 | 1668 | 18 | N
184 | 84818030 | 100 mm nominal dia (Jockey pump Suction) | Nos | 3 | 3 | 1112 | 18 | N
185 | 84818030 | 80 mm nominal dia (Jockey pump Discharge) | Nos | 3 | 3 | 834 | 18 | N
186 | 84818090 | Supplying, Installing, testing and commissioning CI BUTTERFLY VALVES (PN 25) as per BS 5155 sim seal standared lever operated type with required Ranges without lugs, SS-304 disc, nuts, bolts etc. complete The valve shall be fittedirgh Supervisory switch for monitoring
187 |  | Cost of supply and delivery
188 | 84818090 | 150 mm nominal dia | Nos | 8 | 8 | 17375 | 18 | N
189 | 84818090 | 250 mm nominal dia | Nos | 1 | 1 | 41283 | 18 | N
190 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT
191 | 84818090 | 150 mm nominal dia | Nos | 8 | 8 | 1668 | 18 | N
192 | 84818090 | 250 mm nominal dia | Nos | 1 | 1 | 2780 | 18 | N
193 | 7304 | Supplying, installing, testing and commissioning of MS C-Class Pipes/G1 C Class Heavy grade Pipes confirming to 15 12:39 Part 165 3509 Fe 410 grade fimen Ruck wilh painting, suitable type of supports, anchor fasteners, bolts nuts (Hot deep Galvanised), clamps. "U" bolte malleable specials such as Reducers Tees, elbows, flanges, Including cutting, Welding, fixing in/on walls, ceiling by using suitable supports etc, as per drawings. The quoted rate shall also include for chasing/chipping walls, making bore holes in walls/ttoor and making them good with filler material and finished in cement morter etc. complete Fire Sealant at pipe crossingaf waistab to considered in costing (Inside pump room piping only) Note upto 150 mm dia Pipe of Gt & above 150 mm dia MS Pipe.
194 |  | Cost of supply and delivery
195 | 7304 | 300 mm nominal dia | Rmt | 25 | 25 | 5500 | 18 | N
196 | 7304 | 250 mm nominal dia | Rmt | 30 | 30 | 4610 | 18 | N
197 | 7304 | 200 mm nominal dia | Rmt | 20 | 20 | 3614 | 18 | N
198 | 7304 | 150 mm nominal dia | Rmt | 57 | 57 | 2730 | 18 | N
199 | 7304 | 100 mm nominal dia | Rmt | 6 | 6 | 1880 | 18 | N
200 | 7304 | 80 mm nominal dia | Rmt | 15 | 15 | 1337 | 18 | N
201 | 7304 | 25 mm nominal dia | Rmt | 35 | 35 | 410 | 18 | N
202 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT
203 | 7304 | 300 mm nominal dia | Rmt | 25 | 25 | 3336 | 18 | N
204 | 7304 | 250 mm nominal dia | Rmt | 30 | 30 | 2780 | 18 | N
205 | 7304 | 200 mm nominal dia | Rmt | 20 | 20 | 2224 | 18 | N
206 | 7304 | 150 mm nominal dia | Rmt | 57 | 57 | 1668 | 18 | N
207 | 7304 | 100 mm nominal dia | Rmt | 6 | 6 | 1112 | 18 | N
208 | 7304 | 80 mm nominal dia | Rmt | 15 | 15 | 834 | 18 | N
209 | 7304 | 25 mm nominal dia | Rmt | 35 | 35 | 278 | 18 | N
210 | 90261010 | Supply, Installation of Flow meter on Test line to measure 150% of pump flow and suitable to 150mm dia. As per specificied in the Technical Specifications and Drawing
211 |  | Cost of supply and delivery | Nos | 2 | 2 | 69500 | 18 | N
212 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 2085 | 18 | N
213 | 90262000 | Supply and Installation of Pressure gaugesof suitable range for pumpsets with ball valves, siphon, Fittings like unions / colours / reducers etc.
214 |  | Cost of supply and delivery | Set | 12 | 12 | 3960 | 18 | N
215 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Set | 12 | 12 | 1112 | 18 | N
216 | 84818090 | Providing and Foxing electrically operated Tamper Switch and accessories, complete with tap off socket arrangement as required with potential free contact with 2 Nos. NONC The cost of all consumables, accessories, loading & unloading, lead & lift, tools & tackles, machineries & equipments, wastages scaffolding, transportation, packing & forwarding shifting of debris outside the site premises shall be included in the quoted rates.
217 |  | Cost of supply and delivery | Nos | 2 | 2 | 3960 | 18 | N
218 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 2 | 2 | 695 | 18 | N
219 | 8481 | Supply and Installation of Pressure switches of suitable range for pumpsets with ball valves, Fittings like unions / colours / reducers etc.
220 |  | Cost of supply and delivery | Set | 12 | 12 | 2570 | 18 | N
221 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Set | 12 | 12 | 834 | 18 | N
222 | 8215 | Supplying, installing and commissioning C.I.flanged "Y" type Strainer (PN 10) with SS mesh, suitable flanges, nuts, bolts, gaskets etc. complete:- 200 mm diameter.
223 |  | Cost of supply and delivery | Nos | 3 | 3 | 27110 | 18 | N
224 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 3 | 3 | 2224 | 18 | N
225 | 4016 | Supply, installation , testing & commissioning of heavy duty double flanged rubber expansion joit, pressure rating of (PN) for pump inlet
226 |  | Cost of supply and delivery
227 | 4016 | 200 mm | Nos | 4 | 4 | 22950 | 18 | N
228 | 4016 | 150 mm | Nos | 4 | 4 | 18350 | 18 | N
229 | 4016 | 100 mm | Nos | 3 | 3 | 12510 | 18 | N
230 | 4016 | 80 mm | Nos | 3 | 3 | 7367 | 18 | N
231 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT
232 | 4016 | 200 mm | Nos | 4 | 4 | 2224 | 18 | N
233 | 4016 | 150 mm | Nos | 4 | 4 | 1668 | 18 | N
234 | 4016 | 100 mm | Nos | 3 | 3 | 1112 | 18 | N
235 | 4016 | 80 mm | Nos | 3 | 3 | 834 | 18 | N
236 | 5201 | Supplying of (vertically) mounted M. S fabricated pressure vessels made from 8mm M. S. Plate as per I. S. 2062, as below mentioned size high shell with dished ends at top and flat bottom with floor mounting supports including 50 mm outlet, inlet and Branch for Pressure gauge complete. The interior of the tank surface shall be coated with suitably graded Non-Toxic epoxy coating after necessary surface treatment by sand blasting, etc. to prevent corrosion of the vessel and shall be painted externally with 3 coats of enamel paint over one coat of Zinc Chromate primer including all accessories for complete installation as required The Tank shall be complete with 20mm dia. Brass Air Valve (Ball Type), Air relief valve, Stop Valve 20mm Dia, Drain Valve 20mm Dia and Pressure gauge including 20mm dia Mild Steel/Galvanised Pipe and fittings complete as per Technical Specifications and Drawings. Size, dia 200mm X 1200mm height for Hydrant & sprinkler Testing manifold only
237 |  | Cost of supply and delivery | No. | 1 | 1 | 30580 | 18 | N
238 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | No. | 1 | 1 | 4170 | 18 | N
239 | 73069090 | Providing, fixing & installing MS Class-C exhaust pipe and all foxing accessories and hardwares. The exhaust pipes shall be insutated with 75 mm thick mineral wool (density 150 kg/m3) insulation wrapped in chicken mesh and clad with 26 gauge aluminium sheet including all MS epoxy painted support structural as required. The end of the exhaust pipe shall have end cowl for protection from rain & bird screen. The rate shall include all supports, steel brackets etc., as required Fire Sealant at pipe crossingat wallistab to considered in costing. 100 mm dia
240 |  | Cost of supply and delivery | Rmt | 40 | 40 | 2310 | 18 | N
241 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 40 | 40 | 973 | 18 | N
242 | 73063010 | Providing fixing testing and commissioning of 630 mm tong Sleeve of material GI (C CLASS) Considering 230 mm retaining wall & inside with confirming IS 6392-1971 table-E, sleeve flanges of below mentioned sutible size, thickness of flange, nut bolt size as per hole size property fired in retaining RC Pardi walls of UG TANKS Fire Sealant at pipe crossingat wall/slab to considered in costing Note : a) Single side flange as per IS 6392-1971 table-D or E Note : b) in pardi wall puddle flange as per IS 6392-1971 table-D or c) all item should be coated with 80mm micron hot deep galvanised
243 |  | Cost of supply and delivery
244 | 73063010 | 50 mm dia | Nos | 6 | 6 | 2085 | 18 | N
245 | 73063010 | 80 mm dia | Nos | 3 | 3 | 3475 | 18 | N
246 | 73063010 | 100 mm dia | Nos | 2 | 2 | 4865 | 18 | N
247 | 73063010 | 150 mm dia | Nos | 2 | 2 | 9730 | 18 | N
248 | 73063010 | 200 mm dia | Nos | 3 | 3 | 13900 | 18 | N
249 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT
250 | 73063010 | 50 mm dia | Nos | 6 | 6 | 695 | 18 | N
251 | 73063010 | 80 mm dia | Nos | 3 | 3 | 1040 | 18 | N
252 | 73063010 | 100 mm dia | Nos | 2 | 2 | 1390 | 18 | N
253 | 73063010 | 150 mm dia | Nos | 2 | 2 | 2085 | 18 | N
254 | 73063010 | 200 mm dia | Nos | 3 | 3 | 3475 | 18 | N
255 | 8517 | Supply, Fixing, testing & commissioning og item PVR station complete with flange and all accessories. The inlet press as applicable. The outlet pressure shall be 3.50 kg/sq cm 150 mm dia
256 |  | Cost of supply and delivery | Nos | 3 | 3 | 159850 | 18 | N
257 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Nos | 3 | 3 | 13900 | 18 | N
258 | 8414 | Pump Room Ventilation work Supply & Installation of EXHAUST AIR FAN /FRESH AIR FAN WITH AXIAL TYPE (Single Speed Fan) as per technical specification and drawing, min. IE-3 Motor with class F isulation. The total Fan efficiency shall be min 70%. The noise level shall not be more than 70 DBa @ 3m. The minimum external fan static shall as specified below and as explained in the technical specifications. The price shall include starter / control panel for each fans & Isolator for fans required for maintenance purposes. Fan with complete Canvas connection , supporting accessories, vibration isolators, hangers, and support all complete. Each Panel shall be compitable with BMS Integration All Works shall be complete in accordance with Approved Technical Specifications. Approved Technical Data Sheet, Approved drawings, and as per the Engineer's instruction
259 |  | Cost of supply and delivery
260 |  | Capacity- 4100 CFM, 20 mm ESP (Pump Room Exhaust) | Nos | 1 | 1 | 38920 | 18 | N
261 |  | Capacity- 3700 CFM, 20 mm ESP (Pump Room Fresh air with Pre Filter- 90% down to 10 micron) | Nos | 1 | 1 | 31275 | 18 | N
262 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT
263 |  | Capacity- 4100 CFM, 20 mm ESP (Pump Room Exhaust) | Nos | 1 | 1 | 4170 | 18 | N
264 |  | Capacity- 3700 CFM, 20 mm ESP (Pump Room Fresh air with Pre Filter- 90% down to 10 micron) | Nos | 1 | 1 | 4170 | 18 | N
265 | 854419 | POWER & COMMUNICATION CABLING Supply, Installation, Testing and commissioning of Power Cabling to individual Out Fans with Armoured FRLS, XLPE Multistranded Copper conductor PVC Sheathed extemal XLPE insulated extruded cables complete erected with cable ends to end Termination. Cables shall be fixed on the Ceiling with a clamp and fed hom the Ventilation Panel to each fan Location (Cost of clamps shall be inclusive of item). The cost shall also include glanding and termination with double compression gland and bimetallic lugs. All Works shall be complete in accordance with Approved Technical Specifications, Approved Technical Data Sheet, Approved drawings, and as per the Engineer's instruction.
266 |  | Cost of supply and delivery
267 | 85446090 | 3C × 4 Sqmm XLPE Cable | Rmt | 15 | 15 | 220 | 18 | N
268 | 85446090 | 3C × 1.5 Sqmm XLPE Cable | Rmt | 30 | 30 | 110 | 18 | N
269 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT
270 | 85446090 | 3C × 4 Sqmm XLPE Cable | Rmt | 15 | 15 | 62 | 18 | N
271 | 85446090 | 3C × 1.5 Sqmm XLPE Cable | Rmt | 30 | 30 | 55 | 18 | N
272 | 73089090 | CAIRE TRAY Supply & Eraction of heavy duty galvanized Perforated type 1.6mm thick Cable Bays without cover as per Technical Specifications and drawing of following size, suspended from ceiling or fixed vertically on wall / column as per induding necessary supports like anchor butts, hangers, brackets etc. and accessones the Elbows. Bends, Tee requisite support /suspenders, hardware etc. as per site requirement All supporting structure & hardware including nuts & bolts etc. shall be of galvanized iron as approved 100 mm width × 50 mm depth
273 |  | Cost of supply and delivery | Rmt | 10 | 10 | 542 | 18 | N
274 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 10 | 10 | 350 | 18 | N
275 | 85446090 | EARTHING CONDUCTOR Supplying and Laying of following mentioned earthing conductors complete in all respect as per specification, drawing & approval of Client /consultant. 6SWG Cu wire
276 |  | Cost of supply and delivery | Rmt | 10 | 10 | 100 | 18 | N
277 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 10 | 10 | 55 | 18 | N
278 | 87089900 | AIR EXSTHRILITION SHETT METAL WORKS Supply, fabrication & installation of GI Factory made Rectangular ducting Zinc Coating 180 GSM as per SMACNA STANDARDS (strictly to use 24G ductwork instead of 26G ductwork) with System Components from OEM. Rectangular ducting complete with elbows, turning vanes, neoprene/PVC gaskets, GI fully threaded rods, G.I supports / hangers etc. Duct Pressure Class-2 inch W.G with intermediate bracing @ every 1200 mm as per approved shop drawings. The sealant used for general purpose like duct sealing or any other leakage proofing shall have the VOC limit of 500 g/L less water The duct work and duct sealing shall be done as per ASHRAE 90 1 2007, clause 644.2 All Works shall be complete in accordance with Approved Technical Specifications, Approved Technical Data Sheet, Approved drawings, and as per the Engineer's
279 |  | Cost of supply and delivery
280 |  | 24 G (Duct size : Upto m750mm width) | Sqmt. | 40 | 40 | 1280 | 18 | N
281 |  | 22 G | Sqmt. | 15 | 15 | 1350 | 18 | N
282 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT
283 |  | 24 G (Duct size : Upto m750mm width) | Sqmt. | 40 | 40 | 750 | 18 | N
284 |  | 22 G | Sqmt. | 15 | 15 | 675 | 18 | N
285 |  | Supply, Installation, Testing & Commissioning of Powder coated, extruded aluminium Linear Grille With VCD as stated below in 0 deg/15 deg both Way/single way fixed deflection with End Flanges as required and as shown in approved drawings and specifications Powder coating colour & Make shall be as per Architects approvals. All Works shall be complete in accordance with Approved Technical Specifications, Approved Technical Data Sheet, Approved drawings, and as per the Engineer's instruction
286 |  | Cost of supply and delivery | Sqmt. | 1 | 1 | 12510 | 18 | N
287 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Sqmt. | 1 | 1 | 2780 | 18 | N
288 | 3916 | Supply and Installation of GSS Louvers, adjustable damper complete with aluminum wire mesh bird screen in accordance with powder coating and necessary supporting frame for erection as per approved specifications & drawings. Approved RAL. Code and profile from an architect. All Works shall be complete in accordance with Approved Technical Specifications, Approved Technical Data Sheet, Approved drawings, and as per the Engineer's instruction.
289 |  | Cost of supply and delivery | Sqmt. | 2 | 2 | 9035 | 18 | N
290 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Sqmt. | 2 | 2 | 2780 | 18 | N
291 | 8413 | Pump Room Dewatering Work Submersible Thewatering Pump Supply Installation, Testing and Commissioning of electrically driven submersible de watering pumps for pumping water from pump room collection sump to the nearest storm water drain. Pump shall be of cast iron, with vertical discharge port and integrated submersible 3-phase totally enclosed motor insulation class F (155°C) The pump should have a rise pipe a double mechanical seal and semi-open impeller type. The pump should be equipped with a temperature bi-metal sensor for motor protection in case of overheating. The pump should be fitted with suction strainer & handied impeller strength with Maximum particle size 6 to 10mm, lifting handle and 10 m cable. The pumpo shall be provided with. i . suitable control panel indoor wall mounting type with change over switch including dry run protection ii . industrial type electronic liquid level controllers with stainless steel probes/sensors or float switch for automatic operation. iii .1 no. pressure gauge 4" dial with valve tee and fittings. iv . Cast iron lever operated slim seal type butterfly valves of Cl body and spheroidal graphite iron disc (SG iron) with nitrile rubber seal, as per the respective pressure rating/ sq.cm Confrming to BS 5155 / MF6 standards and including a set of GI flanges as per BS-10 table 1 including bolt nuts, Gl washers, and neoprene rubber gaskets complete etc, (nter valve / audco make ) on the suction and delivery side of each pump. v . Slimsel flap type check valve with CI body and cast steel disc as per respective pressuer rating including a set of GI flanges as per BS-10 table 1 including bolt nuts, GI washers, and neoprene rubber gaskets Complete etc., (inter valve / audco make) on the delivery side of each pump. vi . Alarm indication with signal in the event of pump failure etc. vii . The pump shall be suitable for the following requirements: Discharge - 150 LPM each @ 20 M HEAD (1W+ 1 SB)
292 |  | Cost of supply and delivery | Set | 1 | 1 | 30580 | 18 | N
293 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Set | 1 | 1 | 6950 | 18 | N
294 | 7216 | Channel Grating i. Supply and Installation of GI Hot Dip Galvanised Gratings of 300 mm width, fabricated out of 50 X 50 X 6mm thick MS angle. ii. Supplying & Fixing MS angle nosing fabricated out of 40 X 25 X 6 mm thick MS unequal angle with 20 mm dia rod (round) x 75 mm long J shaped welded at 600 mm C/C for anchoring for above item to fix grating. 300 mm wide grating in existing channel
295 |  | Cost of supply and delivery | Rmt | 18 | 18 | 4865 | 18 | N
296 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 18 | 18 | 834 | 18 | N
297 | 3917 | UPVC Pipe i. 'Supply, Installation, testing and commissioning of approved make Unplastisize Polyvinyl Chloride pipes (UPVC) schedule 80 ASTM IPS confirming to ASTM D 1785 & fittings and specials (schedule 80) such as tees, elbows, couplers, bends, enlargers etc, including transition specials i.e. Brass Adaptors (both Male & Female threaded) (where connection with metal is to be made) all confirming to ASTM D 2467, Joints to be made with UPVC solvent cement as per ASTM D-1785, and solvent confirming to ASTM D 2564, fixed in shafts / on terrace with suitable MS angle (50x50x6) iron brackets supports with suitable Gl 10mm "U" clamps with one coat of primer & two coats of enamel paint, bolts, anchor bolts, nuts and washers fixed on shaft walls/outer supports etc., complete. ii.Note: The work shall include cutting, jointing with solvent cement, pressure testing the joints/pipeline for 10 kg/sq.cm hydraulic pressure, for 5 hours etc making holes, including chasing in solid block masonry walls with groove cutting machine to required width and depth, making bores in walls, foundations and RCC slabs, making good the walls and bores in CC or CM 1:3 as applicable, clearing the debris, grouting of concealed pipes, MS hooks for fixing pipes and making good the walls and floors Notes: Rate Quoted shall be inclusive of cost of other consumables like hacksaw blade, solvent for UPVC pipe. 80mm NB (for dewatering sump discharge line)
298 |  | Cost of supply and delivery | Rmt | 75 | 75 | 236 | 18 | N
299 |  | Cost of erection, testing, certification, commissioning and handing over to MbPT | Rmt | 75 | 75 | 70 | 18 | N