## Sheet1
BOQ Item Sr No(unique no - alphanumeric) | HSN / SAC Code (Numeric) | Item Description(Text) | Unit(Text) | Scheduled Qty(Numeric) | Design Qty(Numeric) | Rate Basic(Numeric) | GST %(Numeric) | Non-Scheduled(Yes/No)
11011 | 84249000 | All kinds of soils | cum | 800 | 0 | 125.6696 | 12 | N
13140 | 84249000 | Removal of excavated/slip earth/ debris/ malba from the site of works to any other place outside Railway land/premises, including all excavations, handling, re-handling, loading, unloading and leading, etc. all labour and material as a complete job. Removal of Earth (all kinds of soils)/ROCKS, BOULDERS including mud/slush, slipped earth in catch water drains, side drains, over berms in cutting, water way of bridges, over coping of toe/breast/retaining walls etc. including crossing of nallah, railway tracks, making/repairing approach roads if required, all lead, lift, ascent, descents, or any other obstruction. Earth spoils to be dumped outside the cutting or railway embankments as per direction of Engineer in charge | cum | 600 | 0 | 144.4592 | 12 | N
31051 | 84249000 | All works upto Plinth level | cum | 50 | 0 | 2000.6172 | 12 | N
33062 | 84249000 | OPC 53 grade | Tonne | 77 | 0 | 5841.2812 | 12 | N
41011 | 84249000 | All work upto plinth level, including raft foundation of washable aprons, HS tank, pile cap, footings of FOB, and Platform shelter etc. | cum | 30 | 0 | 2286.7679 | 12 | N
41012 | 84249000 | All work in buildings above plinth level upto floor two level.Centering and shuttering including strutting, propping etc. and removal of form for : | cum | 60 | 0 | 2573.4018 | 12 | N
42011 | 84249000 | Foundations, footings, bases of columns, raft foundation of washable aprons, Pile caps, Footings of FOB etc. | Sqm | 400 | 0 | 172.0268 | 12 | N
42013 | 84249000 | Suspended floors, roofs, landings, balconies, FOB slabs, walkway slabs and access platform | Sqm | 300 | 0 | 359.7232 | 12 | N
42014 | 84249000 | Lintels, beams, plinth beams, bed blocks, girders, bressumers and cantilevers | Sqm | 200 | 0 | 299.9196 | 12 | N
42015 | 84249000 | Columns, pillars, , posts and struts | Sqm | 100 | 0 | 417.6875 | 12 | N
45014 | 84249000 | High yield strength deformed bars | Kg | 8000 | 0 | 66.9286 | 12 | N
51023 | 84249000 | Cement Mortar 1:6 (1 cement : 6 fine sand) | cum | 80 | 0 | 2709.9444 | 12 | N
72141 | 84249000 | 35mm thick including ISI marked stainless steel butt hinges with necessary screws | Sqm | 10.2 | 0 | 1380.5 | 12 | N
81031 | 84249000 | In RSJ, tees, angles and channels | Kg | 4000 | 0 | 78.6992 | 12 | N
81032 | 84249000 | In flats, plates , round or square bars | Kg | 4000 | 0 | 76.004 | 12 | N
99032 | 84249000 | Granite Black. Area of slab 0.10 Sqm to 0.2 Sqm | Sqm | 15 | 0 | 2309.9168 | 12 | N
99033 | 84249000 | Granite Black. Area of slab over 0.2 Sqm but upto 0.5 Sqm | Sqm | 15 | 0 | 2296.8596 | 12 | N
109210 | 84249000 | Providing and fixing 0.55mm TCT Standing Seam/clip-lock Profile for roofing comprising Zincalume / Galvalume base steel of metal thickness 0.5mm and coated with Zinc-Aluminium coating of AZ-150 (150 gsm) as per AS : 13971993 (total of both sides) and permanently colour coated with 20 microns Super Polyester / SMP Colour Coating over a 5 micron primer and back coat of 5 micron over a 5 micron primer. Standing Seam sheets to be profiled to desired length & width of 400mm to 770mm, having profile depth of 31mm to 61 mm with a unique concealed clip made from GI, one portion of the clip (lower) fastened to purlin and upper part gets attached to roofing sheet. Thereby providing an absolutely puncture-less roof wih concealed clip crimped / locked together by a mechanical sewing machine | Sqm | 250 | 0 | 569.4996 | 12 | N
111041 | 84249000 | 1:4 (1cement: 4coarse sand) 12 mm cement plaster of mix - | Sqm | 800 | 0 | 58.3393 | 12 | N
111061 | 84249000 | 1:4 (1cement: 4coarse sand) 20 mm cement plaster of mix | Sqm | 800 | 0 | 79.6875 | 12 | N
115080 | 84249000 | Finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications with two or more coats applied @ 1.25ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr/10sqm | Sqm | 1000 | 0 | 56.3571 | 12 | N
131133 | 84249000 | 25 mm dia. nominal bore | Metre | 3000 | 0 | 250.3499 | 12 | N
131136 | 84249000 | 50 mm dia. nominal bore | Metre | 3000 | 0 | 453.8037 | 12 | N
136150 | 84249000 | Providing and placing on terrace/staging (at all heights) polyethylene water storage tank ISI : 12701 marked with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank | Litre | 50000 | 0 | 6.4501 | 12 | N
138046 | 84249000 | Hoisting, fitting and fixing in position plastic moulded water storage tank including making connection of intake, delivery, outlet and overflow .pipes etc. with all lead and lift upto all stories. Cost of tanks/fittings to be paid separately 5000 ltr Capacity tank | Each | 10 | 0 | 2941.955 | 12 | N
182013 | 84249000 | Demolishing brick work including stacking of serviceable material and disposal of unserviceable material within 50m lead In cement mortar | cum | 45 | 0 | 472.4643 | 12 | N
181021 | 84249000 | 1:2:4 or richer mix with max. 20mm coarse aggregate | cum | 0 | 0 | 599.0714 | 12 | N
1 | 84249000 | Item Description:- Supplying and fixing 65mm dia single hydrant outlet landing valve in gun metal with C.I. hand wheel & tested to 21 Kg/cm2 pressure (Conforming to IS - 5290) with companion flanges, nuts, bolts, washers, gaskets, gun metal cap & chain, etc. complete as specified | Each | 60 | 0 | 7933.5 | 12 | N
2 | 84249000 | Item Description:- Supplying and fixing swinging type wall mounted fire hose reel to IS 884 with fire hose of braided rubber to IS 444 suitably reinforced Dunlop/Fire stone make 19 mm size and 30 M length, with 10 mm tapering branch nozzle in Brass male and female coupling with cut off valve attachment including fixing with approved anchor fasteners and bolts, complete as specified. | Each | 60 | 0 | 10284.2946 | 12 | N
3 | 84249000 | Item Description:- Supplying and fixing 2 lengths of 63 mm dia. canvas hose each 15 m long as per IS 8423, 2 Nos. instantaneous couplings duly bound to the hose as per IS 903 and 1 No. 65mm dia. copper branch pipe with nozzle as per IS 903, complete as specified. | Each | 60 | 0 | 10249.7411 | 12 | N
4 | 84249000 | Item Description:- Supplying and fixing Fire Brigade 150mm size breach inlet connection with four connecting points 65 mm size fixed over 150 mm dia G.I. pipe necessary companion flanges, nuts, bolts, gasket, washers, outlets, necessary bronze coupling connection etc. BS 215, as specified | Set | 4 | 0 | 7160.6518 | 12 | N
5 | 84249000 | Item Description:- Providing and fixing Siamese in breaching assembly in brass with twin 63 mm breaching gun metal male inlets with non return valve, blank caps and drain valve, inlet boxes, gates and air release valves conforming to BS - 5041 Part 3 complete as specified. | Set | 8 | 0 | 7160.6518 | 12 | N
6 | 84249000 | Item Description:- Supplying and fixing weather proof courtyard fire hydrant MS hose cabinet of about 750 mm x 600 mm x 250 mm size made of 3 mm MS plate capable of accommodating two lengths of 65 mm dia canvas hose of 15 m length with locking arrangement and lever for opening the door after breaking glass. Each hose box to be fitted with glass door in front, painted 'FIRE' in red luminous paint. Hinges should be sturdy to bear the weight of fully open door without sagging. Cabinet should be painted two coats of red enamel paint over a primer suitable for fixing to wall/floor with all necessary supports etc. complete as specified | Each | 60 | 0 | 3440.3839 | 12 | N
7 | 84249000 | Item Description:- Supplying and installing multistage direct coupled centrifugal pump or single stage pump as per manufacturer's pump characteristics data, cast iron casing and bronze/phosphor bronze internal parts, make approved by Tariff Advisory Committee for fire duty, capable of discharging 40 Liters, per sec. against 70 meter head, against all losses, complete with TEFC motor (60 H.P / 45 KW) of approved make motor winding with class F insulation suitable for starter as per Fire Brigade / Supply Co. regulations, base plate, foundation bolts, suitable cable entry gland box, pressure guages, etc. and wired for gauges etc. and wired for automatic start on drop of pressure in the wet riser system | Each | 4 | 0 | 221134.7946 | 12 | N
8 | 84249000 | Item Description:- Providing and installing Booster pump of 900 LPM at 40 m. (11 KW/15 HP) head against all losses complete. With suitable motor and base plate. | Each | 4 | 0 | 21552.2143 | 12 | N
9 | 84249000 | Item Description:- Providing and installing jockey pump of 40 - gpm at 70 m. head (11 KW/15 HP) against all losses complete, with suitable motor and base plate all as item No. 7/NS ( relevent Items). | Each | 4 | 0 | 73009.3929 | 12 | N
10 | 84249000 | Item Description:- Providing and fixing automatic motor control center for hydrant, & jockey and booster pumps to suit the HP of motor for the rated capacity and desired head of pumps. MCC shall be provided with suitable starters and controls for 1 No. Hydrant pump (Electrically operated) 1 No. Fire fighting pump (Diesel engine operated) (Common stand by pump for hydrant & sprinkler) 1 No. Jockey pump 2 Nos. Booster pumps at terrace level (Electrical Driven) Comprising of automatic switch unit isolators, pressure switches to set operating pressure, switches rated 500 Volt AC 50 Hz supply for continuous maximum load and Supply company's regulations, contacts of suitable size, internal isolating baffles, terminal boxes for cables suitably screwed, standard 250 volts, 15 Watt bayonet cap, indicator lamps for the respective pumps behind ruby domes suitably protected against damage, interlocking arrangements as per Fire Brigade's stipulations, auxiliary switch/switches to provide warning by lighting of a lamp and hooters for audible alarm both at pump room and main fire console, tripping a circuit breaker connecting the electric supply to leave ample power for Fire pump, if so required. Auxiliary switch to be rated at 5 Amps. 250 volts AC complete with C.T. connected ammeters, volt meters and selector are to be provided on the panels for each starter and incoming switch fuse unit including necessary power and control cabling from panel to respective pumps complete as specified | Each | 2 | 0 | 137244.4821 | 12 | N
11 | 84249000 | Item Description:- Pressure Gauge | Nos | 15 | 0 | 1053.8839 | 12 | N
12 | 84249000 | Item Description:- Pressure Switch | Nos | 15 | 0 | 3931.0446 | 12 | N
13 | 84249000 | Item Description:- Supplying and fixing wrought steel for MS fabricated air vessel in pump room 300 mm dia. And 1200 high on MS stand with necessary arrangement and including the cut off, drain and air release and drain pipes to the channel in pump room. | No | 2 | 0 | 1087.2857 | 12 | N
14 | 84249000 | Item Description:- Fabricating and fixing MS air vessel (air cusion tank) on top of each wet riser 300 mm dia and 1200 mm high with necessary cut off, air release valve to release water hammers and air locks as necessary, including two coats of enamel paint of approved colour over a primer coat after testing, complete as specified | Set | 2 | 0 | 14953.6339 | 12 | N
15 a | 84249000 | Item Description:- Supplying and fixing 200 mm horizontal pot strainer assembly with brass or phosphor bronze working parts, necessary flanges, rubber gasket, etc. complete as specified 150 mm dia. | Each | 12 | 0 | 10109.2232 | 12 | N
15 b | 84249000 | Item Description:- Supplying and fixing 200 mm horizontal pot strainer assembly with brass or phosphor bronze working parts, necessary flanges, rubber gasket, etc. complete as specified 100 mm dia. | Each | 12 | 0 | 8355.0536 | 12 | N
16 a | 84249000 | GI pipe Supply of 150 mm dia. | RM | 900 | 0 | 2407.2321 | 12 | N
16 b | 84249000 | GI pipe Supply of 100 mm dia. | RM | 685 | 0 | 1966.0982 | 12 | N
16 c | 84249000 | GI pipe Supply of 80 mm dia. | RM | 685 | 0 | 1685.0625 | 12 | N
17 | 84249000 | Item Description:- Supplying and fixing 150 mm GI 'C' class pipe including necessary excavation in earth or moorum, bailing or pumping out out water from trenches with shoring wherever necessary, refilling the trenches, removing away the surplus earth or dumping it on site as directed (depth upto 1000 mm) including short lengths and specials are required, fixing supports, painting two coats of approved enamel paint over a coat of approved primer after laying and testing to 13.5 Kg/Sq.cm complete including necessary protective tape or hessian cloth for buried piping complete as specified | RM | 350 | 0 | 1895.8393 | 12 | N
18 | 84249000 | Item Description:- Supplying and fixing ISI grade approved 9 liters capacity galvanized round bottomed fire buckets painted Red and lettered 'FIRE' each with a bracket to hang the bucket on wall or pillar as directed | Nos | 20 | 0 | 176.2232 | 12 | N
19 | 84249000 | Item Description:- Supply & fixing Commissioning of 15 mm size Quartzoide bulb type sprinkler, of rating 68 degree C with required accessories (a) Upright typeRate including all materials, Labours, T&P, transportation and taxes etc. complete | Nos | 300 | 0 | 228.0536 | 12 | N
20 | 84249000 | Item Description:- Supply & Fixing 1.2 mm Aluminium based photo luminescent Signage with UV protection photo luminescent nontoxic, on radio active maintenance free self-glowing Exit sign comprising Zinc sulphate chargeable crystals which glows in dark. Printed on U-10000 photo luminescent aluminium sheet as per site condition. Rate including all materials, Labours, T&P, transportation and taxes etc. complete | sqm | 2700 | 0 | 44.0558 | 12 | N
21 a | 84249000 | Item Description:- Providing, installation, testing of duel plate non return valve of following size confirming to IS: 5312 complete with neoprene gaskets, GI bolt, nuts, washers etc as required. Rats are inclusive of all taxes, transportation, labour & material, fittings etc. Complete 150 mm dia NRV | Each | 6 | 0 | 7430.1696 | 12 | N
21 b | 84249000 | Item Description:- Providing, installation, testing of duel plate non return valve of following size confirming to IS: 5312 complete with neoprene gaskets, GI bolt, nuts, washers etc as required. Rats are inclusive of all taxes, transportation, labour & material, fittings etc. Complete 80 mm dia NRV | Each | 6 | 0 | 3503.7321 | 12 | N
22 a | 84249000 | Item Description:- Providing and fixing butterfly valve P.N. 1.6 with Bronze / Gun Metal seat duly ISI marked complete with bolt, nuts, gaskets, confirming to IS: 13095 of fallowing size as required . Rats are inclusive of all taxes, transportation, labour & material, fittings etc. Complete 150 mm dia. | Each | 25 | 0 | 10129.9554 | 12 | N
22 b | 84249000 | Item Description:- Providing and fixing butterfly valve P.N. 1.6 with Bronze / Gun Metal seat duly ISI marked complete with bolt, nuts, gaskets, confirming to IS: 13095 of fallowing size as required . Rats are inclusive of all taxes, transportation, labour & material, fittings etc. Complete 100 mm dia. | Each | 25 | 0 | 7282.7411 | 12 | N
22 c | 84249000 | Item Description:- Providing and fixing butterfly valve P.N. 1.6 with Bronze / Gun Metal seat duly ISI marked complete with bolt, nuts, gaskets, confirming to IS: 13095 of fallowing size as required . Rats are inclusive of all taxes, transportation, labour & material, fittings etc. Complete 80 mm dia. | Each | 25 | 0 | 6046.875 | 12 | N
23 | 84249000 | Item Description:- Supplying installing jointing , testing and commissioning of following Dia "C" heavy gauge MS pipe confirming to IS: 1239 IS:3589 with accessories like tees, elbow, flanges, joints rubber on wall/ceiling with suitable angle flat iron clamp and dap faster, painting with red oxide primer coat & two coat of postal red synthetic enamel paints making good etc. Complete as required. Rats are inclusive of all taxes, transportation, labour & material, fittings etc. Complete. (i)200 MM Dia (IS 3589) wall thickness 6.35 MM | RM | 50 | 0 | 3910.3125 | 12 | N
24 | 84249000 | Item Description:- Providing & Fixing of 4.5 KG. capacity Carbon dioxide (CO2) fire extinguisher ISI marked confirming to IS: 15683 with delivery hose horn, squeeze grip, release valve, locking arrangement, operation manual ,bracket with two screwed and sleeve complete etc.as required make life guard / G. Tech / Minimax. Rats are inclusive of all taxes, transportation, labour & material, fittings etc. Complete. | Each | 50 | 0 | 11143.5268 | 12 | N
25 | 84249000 | Item Description:- Providing & fixing of 6.00KgABC (store pressure type) fire extinguisher ISI marked confirming to IS: 15683:14609 IS:3589 ABC powder complete with squeeze grip, release valve, locking arrangement, pressure gauge operation manual brackets with two screwed and sleeve complete etc.as required make life guard / G. Tech /safe pro. Rats are inclusive of all taxes, transportation, labour & material, fittings etc. Complete. | Each | 50 | 0 | 6432.7232 | 12 | N